Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150   INSTALLATION OF FERRORESONANT L-828 {L-829} CCR

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing the L-828 {L-829} constant current regulator (CCR) in accordance with these specifications.

This item shall also include all circuit breakers, wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the CCRs in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  L-828 {L-829}.  The L-828 {L-829} CCRs shall be ETL certified according to the requirements of FAA Advisory Circular 150/5345-10 (latest edition) “Specification for Constant Current Regulators and Regulator Monitors.”  The L-828 {L-829} shall be Ferroresonant and shall be 6.6A, 3-step {5-step}, 4kW {2.5kW, 5kW, 7.5kW, 10kW, 15kW, 20kW, 25kW, 30kW}; {20A, 5-step, 15kW, 20kW; 25kW, 30kW}, with an input voltage of 208Vac {220Vac, 240Vac, 347Vac, 380Vac, 400Vac, 480Vac, 600Vac} 60Hz {50 Hz}.  The remote control voltage shall be 120Vac {+48VDC}.  The L-828 {L-829} CCRs shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

150-2.2  EQUIPMENT SUPPLIED.  A quantity of {TBD} FAA L-828 {L-829} CCR{s} shall be supplied.  Each CCR shall include two Instruction Manuals.

150-2.3  CCR.  The CCR shall supply three (6.6A only) {five (6.6A or 20A)} precision output levels to power the airfield lighting circuit.  Output current levels shall be maintained within ±3% at any intensity step.  Nominal output current levels shall be maintained even when 30% of the isolation transformers have open secondaries.  If input power loss occurs, operation shall resume within five seconds after restoration of input power.  The input power factor shall be 0.99 minimum for 2.5kW to 30kW CCRs.  The efficiency shall be 90% minimum for 2.5kW to 25kW CCRs, and 92% efficiency for 30kW CCRs.

The CCR shall use a Ferroresonant design that produces minimal EMI, high efficiency and near unity power factor for AC 150/5345-10 test conditions.  The CCR shall exceed the EMI testing requirements specified in FAA AC 150/5345-10 (current edition).

{In order to minimize space required in the vault, it shall be possible to directly stack two equal 2.5kW – 30kW CCRs using a manufacturer supplied stacking kit.  In addition, it shall be possible to stack different combinations of CCRs assuming the larger CCR is on the bottom.  The height of the CCR shall be 40 inches maximum to allow controls on top of a stacked regulator to be easily reached. }

A single control board shall be used for all versions of the Ferroresonant CCR to make troubleshooting easier and to minimize spare parts.  The CCR shall have output current surge limitation and soft-start to provide maximum airfield lamp protection.  The CCR shall include overcurrent and open-circuit protection.  No tools shall be needed to open a hinged front access door.  To improve safety, no high voltage shall be present inside the front door area.  Lightning protection on both the input and output of the CCR shall be provided.  {An integral CCR output cutout shall be provided.}

{For L-829 CCRs}

150-2.4  L-829.  Each CCR shall include a Distributed Control and Monitoring Device (DCME) on the front door to provide an integrated control and monitoring package.  Inclusion of a DCME with a L-828 CCR provides for FAA L-829 functionality.  The DCME on each CCR shall be equipped with a front-mounted output current digital indicator with an accuracy of 2 percent.  The DCME shall perform all FAA L-829 monitoring functions including measurement of True RMS CCR output current and voltage, detection of lamps-out, loss of input power, incorrect current, overcurrent and open-circuit.  The DCME shall also be capable of displaying CCR output wattage and VA.  The DCME front panel digital display shall be capable of alternately showing all monitored parameters.  In case of system failure, the DCME shall include remote control latching relays that allow the CCR to stay either in the last selected state or to revert to a preset state.

It shall be possible to connect an integrated Insulation Resistance Monitoring System to the DCME by adding only fiber optic connectors and an individual Insulation Resistance Monitoring board.  It shall be possible to connect the DCME to an external control/ monitoring system via a redundant communication network as part of an overall Airfield Lighting Computer System.

CONSTRUCTION METHODS

150-3.1  PLACING THE L-828 {L-829} CCR.  The contractor shall furnish and install each L-828 {L-829} CCR as specified in the proposal and shown in the plans.  The L-828 {L-829} shall be mounted in the vault at the location shown on the plans.

150-3.2  TESTS. The CCR shall be calibrated according to the manufacturer's instructions using a True RMS meter.  An open-circuit test, conducted according to the manufacturer's instructions, shall also be performed.  The CCR shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance.  The test shall include operating the constant current regulator in each step (Local and Remote) not less than 10 times at the beginning and end of the 24-hour test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for one L-828 {L-829} CCR, and two Instruction Manuals (per CCR) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of L-828 {L-829} CCR installed, in place by the Contractor, and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	L-828 {L-829} CCR, in Place—per each

END OF ITEM L-150