SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150  INSTALLATION OF MEDIUM INTENSITY L-861(L) and L-861E(L) LED LIGHTS

DESCRIPTION

150-1.1 This item shall consist of furnishing and installing the Medium Intensity L-861(L) and L-861E(L) LED fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  L-861.  The L-861(L) and L-861E(L) LED fixtures shall conform to the requirements of the current edition of FAA Advisory Circular 150/5345-46 “Specification for Runway and Taxiway Light Fixtures” and “FAA Engineering Brief No. 67 “Light Sources other than Incandescent and Xenon for Airport Lighting and Obstruction Lighting Fixtures.”  The L-861(L) LED fixture shall be ETL certified.  {The fixture shall also conform to ICAO Annex 14 paragraphs 5.3.9.7, 5.3.9.8 and 5.3.9.9.}  The L-861(L) and L-861E(L) LED fixtures shall be the “EMIS-L” fixture as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

{If required by the airport authority, a Return on Investment (ROI) and Life Cycle Cost (LCC) analysis shall be calculated to validate the benefit of the LED fixture in comparison to the equivalent incandescent technology.}

150-2.2  EQUIPMENT SUPPLIED.  FAA L-861(L) and L-861E(L) LED fixtures shall be supplied for the total quantity as shown on the plans.  Each lot shipment of fixtures shall include one Instruction Manual.  It shall be possible to download additional manuals from the manufacturer’s web site.

150-2.3  L-861(L) AND L-861E(L) LED FIXTURE.  The light source shall be an electroluminescent diode (LED) assembly.  The lifetime of the LED shall be a minimum of 56,000 hours at full intensity and more than 150,000 hours in actual operating conditions. To insure high daytime visibility, the yellow side of an L-861 and the red or green side of an L-861E shall use an outer colored optical lens.

The light fixture, with heater, shall operate on a 6.6A or 20A circuit at 50/60 Hz using an appropriately-sized isolation transformer.  The fixture shall be designed to operate with a 30/45W, 6.6A (secondary) isolation transformer, allowing existing incandescent fixture transformers to be reused.  The L-861(L) fixture load with the heater inactive shall be no more than 15VA and shall use a 10/15W isolation transformer.  The bi-directional L-861E fixture load with the heater inactive shall be no more than 10VA and shall use a 10/15W isolation transformer.  {The L-861(L) fixture load with the heater operational shall be no more than 35VA and shall use a 30/45W isolation transformer.  The bi-directional L-861E(L) fixture load with the heater operational shall be no more than 30VA and shall use a 30/45W isolation transformer.  The heater shall be designed to insure that the light emitting area remains unobscured and clearly visible in a manner similar to existing incandescent fixtures.  Activation of the heater shall be thermostatically controlled.  To insure long reliability, the heater shall be mounted in the body of the fixture.  Heater wires taped to the inside optical element, that are subject to long-term degradation, shall not be used.}

The fixture shall have a leveling mechanism that allows ±4° vertical adjustment in the field.  It shall be possible to install the lights on existing circuits in addition to, or in replacement of, conventional incandescent or halogen lights without having to change any other element (CCR, primary and secondary cabling, series isolation transformer, etc.).  The fixture light output shall match quartz-incandescent fixtures at all brightness levels on a 3-step or 5-step regulator.

It shall be possible to easily remove the top optical assembly without the use of tools.  Exterior, hard to remove, rubber type elements (that are subject to UV degradation; attack by rodents, fire ants, birds, etc) shall not be used to hold the top optical assembly on.  The corset entry into the fixture shall be sealed to prevent insects from entering into the fixture.

The fixture shall use robust, solid-state internal devices that withstand damage if the fixture is knocked over.   The overall fixture height shall be 14 inches {24 inches} {30 inches}.

CONSTRUCTION METHODS

150-3.1  PLACING THE L-861(L) AND L-861E(L) LED FIXTURES.  The contractor shall furnish and install each L-861(L) and L-861E(L) LED fixture as specified in the proposal and shown in the plans.  The L-861(L) LED and L-861E(L) fixtures shall be mounted on an industry standard 1.5-inch {2-inch} slip fit hubbed frangible coupling.  The fixture shall then be mated to a standard FAA L-867 base at the locations shown on the plans.

150-3.2  TESTS.  All runway edge and end lights shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance.  The test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test.  The fixtures shall illuminate properly during each portion of the test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of lights to be paid for under this item shall be for the total quantity of L-861(L) and L-861E(L) LED fixtures installed and one Instruction Manual (per lot) accepted as completed units, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of L-861(L) and L-861E(L) LED fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	L-861(L) and L-861E(L) LED fixtures, in Place—per each

END OF ITEM L-150