SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150  INSTALLATION OF LED IN-PAVEMENT TAXIWAY FIXTURES

DESCRIPTION

150-1.1 This item shall consist of furnishing and installing the {L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the light fixtures in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  LED IN-PAVEMENT FIXTURE.  The LED in-pavement fixture shall conform to the requirements of FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures” and FAA Engineering Brief No. 67 (current edition) “Light Sources other than Incandescent and Xenon for Airport Lighting and Obstruction Lighting Fixtures.”  The fixtures shall be ETL certified and listed in AC 150/5345-53 (current edition), Appendix 3 at the time of bid.  The LED in-pavement fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

{If required by the airport authority, a Return on Investment (ROI) and Life Cycle Cost (LCC) analysis shall be calculated to validate the benefit of the LED fixture in comparison to the equivalent incandescent technology.}

150-2.2  EQUIPMENT SUPPLIED.  A quantity of {TBD} in-pavement fixtures shall be supplied.  Each lot shipment shall include one Instruction Manual.  The manufacturer shall also have a downloadable electronic version of the manual available on their web site.

To insure reduced energy, runway down time and maintenance requirements, the in-pavement fixture shall utilize a Light Emitting Diode (LED) light source.  The {L-852A} {L-852B} {L-852C} fixture shall use no more than one LED per side. The {L-852D} {L-852J} {L-852K} shall use no more than two LEDs per side.  For the {L-852A} {L-852B} {L-852C} fixture, the average lifetime of the LED shall be a minimum of 100,000 hours at full intensity and more than 200,000 hours in actual operating conditions. For the {L-852D} {L-852J} {L-852K} fixture, the average lifetime of the LED shall be a minimum of 56,000 hours at full intensity and more than 150,000 hours in actual operating conditions.

150-2.3  FIXTURE POWER.  The light fixture shall operate on either a 2.8A to 6.6A or 8.5A to 20A circuit using an appropriately-sized isolation transformer.  To minimize spare parts requirements, the fixture internal power supply circuit shall be the same for 3-step or 5-step series circuits.  The fixture shall operate on any 3- or 5-step ferroresonant or thyristor CCR that is designed in compliance with FAA requirements specified in AC 150/5345-10 (current edition).

An option for a heater shall be available for the fixture.  To reduce overall energy consumption, the heater shall be thermostatically controlled.

It shall be possible to install the lights on existing circuits in addition to, or in replacement of, conventional incandescent or halogen lights without having to change any other element (CCR, primary and secondary cabling, series transformer, etc.). The fixture light output shall match quartz-incandescent fixtures at all brightness levels on a 3-step and 5-step regulator.  The required beam color shall be obtained without the use of a color filter.

“Smart electronics” shall control current to the LED, so that the light output matches existing incandescent fixtures at all brightness levels without sacrificing any light characteristics.  To insure reduced risk of inadvertent light output switching, the actual light output shall be determined based on a continuous light output curve and not separate discrete steps.  This insures light output truly represents input current, even if series circuit input current is not within FAA specification limits.  To reduce the risk of inadvertent light output variation (such as when a series circuit fault is occurring), the fixture electronics shall incorporate a time delay before switching to a new light output setting.

The fixture bottom cover shall include an earth ground terminal.

The {L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixture shall be Style 3 ( ¼ inch above grade) and the top cover shall be of single piece construction (2 piece top covers will not be allowed) and made from an aluminum alloy to enhance fixture strength.  All components shall be corrosion proof without the use of environmentally hazardous metal protective coatings, such as cadmium plating.  The prisms shall be field replaceable without the use of epoxy or other sealing compounds and held in place by means of a mechanical clamping device.  Grommets, in conjunction with a mechanical clamping device, shall be used for the entry and sealing of L-823 cord set wire cables to the inner cover.  This will allow for cord set replacement without the use of epoxy or other sealing compounds.  A test port with removable plug will be provided in the bottom cover to allow for pressure testing after fixture overhaul.  To insure fixture quality, the manufacturer will production leak and dielectric strength test each individual fixture prior to shipment.  The leak test will be by means of a Helium tank testing apparatus, capable of detecting minor fixture leaks due to material porosity.

CONSTRUCTION METHODS

150-3.1  PLACING THE LED IN-PAVEMENT FIXTURE.  The contractor shall furnish and install each {L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixture as specified in the proposal and shown in the plans.  {L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixtures shall be mounted on industry standard FAA L-868 base cans as specified and shown by location on the plans.

150-3.2  TESTS.  Each fixture shall be connected to the series circuit using the manufacturer’s recommended isolation transformer.  The constant current regulator (CCR) shall then be tested to verify the correct output current is present at each step.  The output current shall be checked with a True RMS meter using the CCR manufacturer’s instructions.  The entire circuit shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance.  The test shall include operating the CCR in each step (Local and Remote) not less than 10 times at the beginning and end of the 24-hour test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for [TBD] {L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixtures, and 1 Instruction Manual (per lot) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of LED in-pavement fixtures installed, in place by the Contractor, and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	{L-852A, L-852B, L-852C, L-852D, L-852J, L-852K} LED in-pavement fixture, in Place—per each

END OF ITEM L-150