F-RANGE QUARTZ IN-PAVEMENT FIXTURE – SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150  INSTALLATION OF QUARTZ IN-PAVEMENT FIXTURE

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing the {L-850A, L-850B, L-850C, L-850D, L-850E, L-850F, L-852A, L-852B, L-852C, L-852D, L-852G, L-852S, L-852G/S, L852T, High Intensity Approach FAA-E-2952, MALSR Approach FAA-E-2968} in-pavement fixture in accordance with these specifications.

This item shall also include all wire and cable connections and the furnishing and installing of all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the in-pavement fixtures in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  IN-PAVEMENT FIXTURE.  The {L-850} {L-852} in-pavement fixtures shall be FAA certified according to the requirements of FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures”, and listed in AC 150/5345-53 (current edition), Appendix 3 at the time of bid.  {The high intensity in-pavement approach fixture shall be designed according to FAA-E-2952.} {The MALSR in-pavement approach fixture shall be designed according to FAA-E-2968}.  The in-pavement fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

150-2.2  EQUIPMENT SUPPLIED.  A quantity of {TBD} in-pavement fixtures shall be supplied.  Each lot shipment shall include one Instruction Manual.  The manufacturer shall also have a downloadable electronic version of the manual available on their web site.

The {L-850A, L-850B, L-850C, L-850D, L-850E, L-850F, L-852A, L-852B, L-852C, L-852D, L-852G, L-852S, L-852G/S, L852T, High Intensity In-pavement Approach Fixture FAA-E-2952, MALSR In-pavement Approach Fixture FAA-E-2968} top cover shall 12” diameter and be made from an aluminum alloy to enhance fixture strength.  All components shall be corrosion proof without the use of environmentally hazardous metal protective coatings, such as cadmium plating.  The prisms shall be field replaceable without the use of epoxy or other sealing compounds and held in place by means of a mechanical clamping device.  Grommets, in conjunction with a mechanical clamping device, shall be used for the entry and sealing of L-823 cord set wire cables to the inner cover.  This will allow for cord set replacement without the use of epoxy or other sealing compounds.  A test port with removable plug will be provided in the bottom cover to allow for pressure testing after fixture overhaul.  To insure fixture quality, the manufacturer will production leak and dielectric strength test each individual fixture prior to shipment.  The leak test will be by means of a Helium tank testing apparatus, capable of detecting minor fixture leaks due to material porosity.  The actual fixture bid shall have an installed history with a minimum of three years at five sites with negligible failure history.

{The L-850A fixture shall be Style 3 ( ¼ inch above grade) and shall use two 48W lamps rated 1500 hrs at full intensity for bi-directional applications.  To minimize spare parts requirements, the 48W lamp shall be interchangeable with the one used on quartz L-858 signs.  The top cover shall be made of a single piece, 12” construction (2- piece top covers will not be allowed). }

{The L850B fixture shall be Style 3 ( ¼ inch above grade) and shall use one 48W rated 1500 hrs at full intensity.  To minimize spare parts requirements, the 48W lamp shall be interchangeable with the one used on quartz L-858 signs.  The top cover shall be made of a single piece, 12” construction (2- piece top covers will not be allowed). }

{The L-850C fixture shall be Style 3 ( ¼ inch above grade) and shall use two 105W lamps rated 1000 hrs at full intensity for bi-directional applications.}

{The L-850D fixture shall be Style 2 ( ½ inch above grade) and shall use one 62W lamp rated 1000 hrs at full intensity for FAA Runway Threshold applications and no more than two 62W lamps for FAA Runway End applications.}

{The L-850E fixture shall be Style 2 ( ½ inch above grade) and shall use no more than two 105W lamps rated 1000 hrs at full intensity for FAA uni-directional Runway Threshold applications.}

{The L-850F fixture shall be Style 3 ( ¼ inch above grade) and shall use two 48W lamps rated 1500 hrs at full intensity for uni-directional applications.  To minimize spare parts requirements, the 48W lamp shall be interchangeable with the one used on quartz L-858 signs. }

{For two-lamp bi-directional L-852A through D applications, the fixture shall be Style 3 ( ¼ inch above grade) and shall use two 30W lamps rated 1500 hrs at full intensity.}

{For single-lamp uni or bi-directional L-852A/L-852C applications, the fixture shall be Style 3 ( ¼ inch above grade) and shall use one 45W lamp rated 1000 hrs at full intensity.}

{The L-852G fixture shall be Style 3 ( ¼ inch above grade) and shall use one 105W lamp rated 1000 hrs at full intensity for uni-directional applications.}

{The L-852S fixture shall be Style 3 ( ¼ inch above grade) and shall use one 105W lamp rated 1000 hrs at full intensity for uni-directional applications.  The top cover shall be made of a single piece, 12” construction (2- piece top covers will not be allowed). }

{The L-852G/S fixture shall be Style 3 ( ¼ inch above grade) and shall use two electrically and optically separate 105W lamps rated 1000 hrs at full intensity for uni-directional applications.  The top cover shall be made of a single piece, 12” construction (2- piece top covers will not be allowed). }

{The L-852T fixture shall be Style 2 ( ½ inch above grade) and shall use one 45W prefocused halogen lamp with an expected life of more than 1,000 hours at full intensity.}

{The High Intensity In-pavement Approach fixture shall be  ½ inch above grade and shall use a maximum of three 105W lamps rated 1000 hrs at full intensity.  The fixture shall be in photometric compliance with FAA-E-2952 (Current Edition).  Major parts of the light shall be made from aluminum alloy and shall not exceed 18 pounds (without adapter ring(s)).  The maximum slope of any part of the top cover shall not exceed 20 degrees.}

{The MALSR In-pavement Approach Threshold (Style II-green) fixture shall be  ½ inch above grade and shall use a maximum of three 62W lamps rated 1000 hrs at full intensity.  The fixture shall be in photometric compliance with FAA-E-2968 (Current Edition).  Major parts of the light shall be made from aluminum alloy and shall not exceed 18 pounds.  The maximum slope of any part of the top cover shall not exceed 20 degrees.}

{The MALSR Medium Intensity In-pavement Approach (Style I-white) fixture shall be  ¼ inch and shall use one 105W lamp rated 1000 hrs at full intensity.  The fixture shall be in photometric compliance with FAA-E-2968 (Current Edition).  Major parts of the light shall be made from aluminum alloy and shall not exceed 18 pounds.  The maximum slope of any part of the top cover shall not exceed 4 degrees.}

CONSTRUCTION METHODS

150-3.1  PLACING THE IN-PAVEMENT FIXTURE.  The contractor shall furnish and install each in-pavement fixture as specified in the proposal and shown in the plans.  Each in-pavement fixture shall be mounted on the appropriate base can at the location shown on the plans.

150-3.2  TESTS.  Each fixture shall be connected to the series circuit using the manufacturer’s recommended isolation transformer.  The constant current regulator (CCR) shall then be tested to verify the correct output current is present at each step.  The output current shall be checked using the CCR manufacturer’s instructions using a True RMS meter.  The entire circuit shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance.  The test shall include operating the (CCR) in each step (Local and Remote) not less than 10 times at the beginning and end of the 24-hour test.

{For MALSR Approach FAA-E-2968 fixtures}

150-3.2  TESTS.  Each fixture shall be connected to the power circuit using the manufacturer’s recommended isolation transformer.  The AC power source shall then be tested to verify the correct isolation transformer output current is present at each step.  The output current shall be checked using the fixture manufacturer’s instructions using a True RMS meter.  The entire circuit shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance.  The test shall include operating AC power source at each step not less than 10 times at the beginning and end of the 24-hour test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for [TBD] {L-850A, L-850B, L-850C, L-850D, L-850E, L-850F, L-852A, L-852B, L-852C, L-852D, L-852G, L-852S, L-852G/S, L852T, High Intensity Approach FAA-E-2952, MALSR Approach FAA-E-2968} in-pavement fixtures, and 1 Instruction Manual (per lot) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of in-pavement fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1  {L-850A, L-850B, L-850C, L-850D, L-850E, L-850F, L-852A, L-852B, L-852C, L-852D, L-852G, L-852S, L-852G/S, L852T, High Intensity Approach FAA-E-2952, MALSR Approach FAA-E-2968} in-pavement fixture, in Place—per each

END OF ITEM L-150