SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150  INSTALLATION OF L-862 and L-862E LIGHTS (clamp band)

DESCRIPTION

150-1.1 This item shall consist of furnishing and installing the L-862 {L-862E} fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  L-862 {L-862E}.  The L-862 {L-862E} fixtures shall conform to the requirements of FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures”. The L-862 {L-862E} fixture shall be ETL certified.  The L-862/E fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

150-2.2  EQUIPMENT SUPPLIED.  L-862 {L-862E} fixtures shall be supplied for the total quantity as shown on the plans. Each lot shipment of fixtures shall include two Instruction Manuals.

150-2.3  FIXTURE.  The L-862 high intensity elevated light fixtures shall be used to delineate the edges of airport runways. {L-862E high intensity elevated light fixtures shall be used to delineate the threshold/end of airport runways.}

The fixture shall use a 120W, 6.6A quartz lamp. The lamp life shall be 500 hours at 6.6A.

The fixture shall have a single-latch, stainless steel clamp band that allows easy removal of the lens for lamp changes. The top casting shall hold the outer globe, which shall be indexed to the lens for proper photometric performance. Two prismatic inner lens segments shall be mounted inside on a socket mounting plate assembly. The fixture shall be leveled after installation via four screws that allow a 4° leveling adjustment. The fixture shall have use an aluminum head assembly and stainless steel hardware, and shall be protected with aviation yellow enamel paint. The fixture shall be weather-resistant to rain, snow, ice and standing water. The lens shall be made from heat- and shatter-resistant glass.

CONSTRUCTION METHODS

150-3.1  PLACING THE FIXTURES.  The contractor shall furnish and install each L-862 {L-862E} fixture as specified in the proposal and shown in the plans. The L-862 {L-862E} fixtures shall be mounted on a 12-inch base plate with a 1.5-inch threaded hub.  The base plate shall be mounted to a standard FAA L-867B base can at the locations shown on the plans. {A 30-inch galvanized angle iron stake shall be available for stake mounting applications.} The overall fixture height shall be 14 inches {20 inches} {24 inches} {30 inches}.

150-3.2  TESTS.  All L-862 {L-862E} lights shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance. The test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test. The fixtures shall illuminate properly during each portion of the test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of lights to be paid for under this item shall be for the total quantity of L-862 {L-862E} fixtures installed and two Instruction Manuals (per lot) and accepted as completed units, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of L-862 {L-862E} fixtures installed, in place by the Contractor, and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	L-862 {L-862E} fixtures, in Place—per each

END OF ITEM L-150