SAMPLE SPECIFICATION

Note:  Modify the items in italics according to your specific job requirements.

ITEM L-150  INSTALLATION OF COVERT INFARED IN-PAVEMENT FIXTURE

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing a covert in-pavement fixture in accordance with these specifications. The covert fixture shall be a modification of a FAA L-850A fixture. The fixtures shall be shipped complete from the manufacturer and shall not require any field assembly or modification including any infrared filtering or sealing.

This item shall also include all filters, wire and cable connections and the furnishing and installing of all necessary mounting structures. It shall also include the testing of the installation and all incidentals necessary to place the in-pavement fixtures in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  IN-PAVEMENT FIXTURE.  The L-850A fixture shall meet the applicable requirements (excluding photometrics) contained in FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures; FAA Engineering Brief No. 67 (current edition). The covert in-pavement fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

150-2.2  EQUIPMENT SUPPLIED.  A quantity of [TBD] covert in-pavement fixtures shall be supplied. Each lot of in-pavement fixtures shall include two Instruction Manuals.

150-2.3  COVERT FIXTURE.  Covert fixtures shall be defined as those which produce no visible light output, but rather infrared emissions to be used by pilots wearing night vision goggles. Technical specifications of these fixtures are of the utmost importance.

The in-pavement (IR) fixture must meet the following performance requirements:

- The IR fixture must meet all L-850A requirements in FAA Advisory Circular 150/5345-46C except photometry per paragraph 3.3. The L-850A shall be modified with a ADB SAFEGATE IR fixture part number 44A6659/XXXX or equal.

- Irradiance requirements shall be as follows:

  - The main beam coverage shall be ±5° horizontal and 0.2 to 9° vertical. Each irradiance reading must measure total irradiance from 750 to 900nm. Irradiance must be measured along the horizontal (at 4.6° vertical) and vertical (at 0° horizontal) axes at intervals of a maximum of 1 degree – a minimum of ten readings on each axis must be taken. The average value of each axis must be at least 18µW/cm2.

  - Irradiance below 700nm shall be no more than 2x10-10µW/cm2. In addition, peak irradiance shall be between 800 to 850nm.

- When testing irradiance, the fixture must be operated with a 6.6A AC input current for 15 minutes before taking the measurements. Irradiance must be tested at a distance of 50cm.

The in-pavement infrared (IR) fixture manufacturer must provide a FAA accepted third party test lab (Intertek) test report certifying that all the above requirements are met.

150-2.4  L-850A REQUIREMENTS.  The L-850A top cover shall be of single piece, 12” construction (2 piece top covers will not be allowed) and made from an aluminum alloy to enhance fixture strength. All components shall be corrosion proof without the use of environmentally hazardous metal protective coatings, such as cadmium plating. The prisms shall be field replaceable without the use of epoxy or other sealing compounds and held in place by means of a mechanical clamping device. Grommets, in conjunction with a mechanical clamping device, shall be used for the entry and sealing of L-823 cord set wire cables to the inner cover. This will allow for cord set replacement without the use of epoxy or other sealing compounds. A test port with removable plug will be provided in the bottom cover to allow for pressure testing after fixture overhaul. To insure fixture quality, the manufacturer will production leak and dielectric strength test each individual fixture prior to shipment. The leak test will be by means of a Helium tank testing apparatus, capable of detecting minor fixture leaks due to material porosity. The actual fixture bid shall have an installed history with a minimum of three years at five sites with negligible failure history.

The L-850A fixture shall be Style 3 (( ¼ inch above grade) and shall use one 48W, 6.6A lamps [two 48W, 6.6A lamps] rated 1500 hours at full intensity.

CONSTRUCTION METHODS

150-3.1  PLACING THE IN-PAVEMENT FIXTURE.  The contractor shall furnish and install each in-pavement fixture as specified in the proposal and shown in the plans. Each in-pavement fixture shall be mounted on the appropriate base can at the location shown on the plans.

150-3.2  TESTS.  Each fixture shall be connected to the series circuit using the manufacturer’s recommended isolation transformer. The constant current regulator (CCR) shall then be tested to verify the correct output current is present at each step. The output current shall be checked using the CCR manufacturer’s instructions using a True RMS meter. The entire circuit shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance. The test shall include operating the (CCR) in each step (Local and Remote) not less than 10 times at the beginning and end of the 24-hour test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for [TBD] Covert in-pavement fixtures, and 2 Instruction Manuals (per lot) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of in-pavement fixtures installed, in place by the Contractor, and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1  L-850A covert IR in-pavement fixture, in Place—per each

END OF ITEM L-150