<Insert Engineering Logo here>

Technical Specification for

Airfield Lighting Control and Monitoring System

Programmable Logic Controller (PLC) architecture

[Airport’s Project Title]

[Airport Name]

[City, State]

Project Number: [XXX-XXXXX]

<Insert Engineering Address here>

Table of Contents

1.	Introduction	1-1

1.1	Background	1-1

1.2	Qualifications	1-1

1.3	Project Scope	1-1

1.4	Project Coordination	1-2

1.5	Production Test	1-3

1.6	Contractor Installation Requirements	1-3

1.7	Contractor Power-up and Initial Testing	1-5

1.8	ALCS Manufacturer PLC Commissioning	1-6

1.9	System Acceptance Test (SAT)	1-6

1.10	Manuals	1-6

1.11	As-Installed Drawings	1-6

1.12	On-site Training	1-7

1.13	Owner System Acceptance and Warranty Start Date	1-8

1.14	System Warranty	1-8

1.15	System Service and Support	1-8

1.16	Spare Parts Package	1-9

2.	Equipment and Materials	2-1

2.1	General	2-1

2.2	Communication Network	2-2

2.3	Vault Equipment	2-5

2.4	Tower Equipment	2-10

2.5	Touchscreen Panel Computer	2-11

3.	Man-Machine Interface Operation	3-1

3.1	General	3-1

3.2	Overview of Operation	3-1

3.3	Touchscreen Command Sequences	3-2

3.4	Touchscreen Control Methodology	3-2

3.5	Touchscreen Graphics	3-3

3.6	Vault Emergency Generator Control	3-4

3.7	Vault Automatic Transfer Switch (ATS) and Generator Monitoring	3-4

3.8	Navigational Aid Control	3-4

3.9	Radio Control Enabled Control Methodology	3-5

# Introduction

## Background

- The airfield lighting Programmable Logic Controller (PLC) system shall combine state-of-the-art programming intelligence with high quality industrial strength components.

- The system shall represent the leading edge in aviation lighting technology using programmable logic control equipment.

## Qualifications

- The ALCMS manufacturer shall be ISO 9001 certified and provide copy of certification during bidding process.

- The ALCMS manufacturer shall be listed in the FAA Approved Equipment List, AC 150/5345-53 (current edition), and a FAA approved supplier of L-890 ALCMS in accordance with AC 150/5345-56, and Monitors and Regulators in accordance with AC 150/5345-10 (current edition).

- The ALCMS manufacturer shall have demonstrated a minimum of five (5) years of experience in airfield lighting control and monitoring systems.  The control system manufacturer shall have at least five (5) control and monitoring systems of similar size and complexity.

## Project Scope

- The ALCMS manufacturer shall furnish and commission a complete and functional control and monitoring system based on an industry standard Ethernet network.

- This project shall include software, programming, PLC, manuals, on-site commissioning, on-site testing, on-site training and any other materials, tools and equipment to provide a fully functional system to the satisfaction of the owner.

## Project Coordination

- The ALCMS manufacturer shall provide an experienced and qualified Engineering, Sales and Service staff to support contractor and airport throughout the installation and life of the system.

- The project shall follow this basic cycle of events:

|  | Milestone | Description |
| --- | --- | --- |
| 1. | Submittal | The manufacturer shall submit specifications to the contractor |
| 2. | Submittal Review and Approval | Submittal is reviewed by the contractor, airport, and engineers |
| 3. | Production Release | The manufacturer shall release approved system to manufacturing |
| 4. | Production | System is manufactured |
| 5. | Production Testing | System is tested by the manufacturer prior to shipment. Production test reports shall be available upon request. |
| 6. | Shipment of system | PLC system is shipped to job site for installation by Contractor |
| 7. | Installation | Contractor installs equipment and completes external wiring |
| 8. | Power-up | The Contractor completes PLC system power-up and initial control testing to verify installation, communication and wiring |
| 9. | Commissioning | The manufacturer shall arrive at installation site to complete commissioning of system and verify operation |
| 10. | System Readiness Check | The manufacturer performs a system readiness check confirming proper operation prior to cutting over system |
| 11. | System Cut-over | The manufacturer and Contractor shall cut over the new system and bring it on-line and operational |
| 12. | System Acceptance Testing | System is available for System Acceptance Testing (SAT) which shall be witnessed the by airport/owner and/or engineer. |
| 13. | Manuals / As-Built drawings | The manufacturer shall issue operator manuals, maintenance manuals and ATC manuals and final as-built drawings. |
| 14. | On-Site Training | The manufacturer shall complete on-site training of maintenance and ATC personnel |
| 15. | Final Owner Acceptance | Upon completion of all contractual requirements, system is accepted in writing by the airport/owner |
| 16. | Warranty and Support | The manufacturer shall provide warranty and support per the contractual requirements |

## Production Test

- Before shipment, the PLC system shall be assembled as an operating system at the manufacturer’s test facilities.

- The manufacturer shall make the production testing available for representative(s) of the airport/owner and engineer to witness the testing of the system if requested.

- The manufacturer shall complete production and operational testing prior to shipment of equipment to the project site.

- Production testing reports shall be made available upon request.

## Contractor Installation Requirements

- The installing contractor shall be responsible for the physical installation of all associated PLC components.  At a minimum, this includes the Constant Current Regulators (CCRs), PLC cabinets, Touchscreen control stations and other control equipment.

- The Contractor shall furnish, install, relocate, connect and test all equipment, equipment accessories, conduit cables, wires, buses, grounds and support necessary to insure a complete and operable electrical distribution facilities for the airport lighting system as specified herein the submittal package.

- The equipment installation and mounting shall comply with the requirements of the National Electrical Code and local code agency having jurisdiction.

### Wire and Connections

- The Contractor shall make all necessary electrical connections at each location in accordance with the ALCMS manufacturer’s wiring diagrams.

- All wires called out in the drawings associated with equipment that is to be controlled or monitored should be pulled, terminated and dressed at the appropriate terminal blocks and at the associated equipment.

- In wiring to the terminal blocks, the Contractor shall leave sufficient extra length on each control lead to make future changes in connections at the terminal block.

### Marking and Labeling

- All equipment, control wires, terminal blocks, etc., shall be tagged, marked or labeled as specified below:

- Wire Identification: The Contractor shall furnish and install self-sticking wire labels or identifying tags on all control wires at the point where they connect to the control equipment or to the terminal blocks.

- Wire labels, if used, shall be of the self-sticking, pre-printed type and of the manufacturer’s recommended size for the wire involved.  Identification markings designated in the plans shall be followed.

- Tags, if used, shall be nonferrous metal or plastic.  Each tag shall be securely tied to the proper wire by a nonmetallic cord or plastic wire tie.

### Installation of Data Cables

- The Contractor shall install, terminate and test all data cables required for the project.  This includes all of the following components: Data cable, Terminal cabinets, Jumper cables

- All associated data cables shall be tested upon completion of the cable installation and termination of connectors.

- Tests shall include verification of point-point continuity of each wire.

- All test data shall be recorded and composed into a test report and shall be submitted to the airport / owner for approval.

- Commissioning of the system shall not begin until all test reports are submitted and approved and a copy provided to manufacturer.

<Engineer must determine type and quantity of communication needed. Typical design for a PLC system is one or two fiber optic communication links.  Installation sample specifications are provided as follows and can be removed if not included>

### Contractor Fiber Optic Communication Equipment Installation

- The Contractor shall install, terminate and test all fiber optic communications required for the project.  This includes all of the following components:

- Fiber optic cable

- Fiber optic patch panels

- Fiber optic jumper cables

- Fiber connectors / couplings

- Fiber junction Boxes

- Installation of the fiber optic communication equipment shall be done by a trained and qualified fiber optic specialist.

- The qualifications of the company and specialist to install the fiber optic equipment shall be submitted to the airport / owner for approval.

- All associated fiber optic equipment including fiber cables, splices, jumper cable shall be tested upon completion of the fiber cable installation and termination of connectors.

- Tests shall include verification that the ‘dB loss versus the distance of the fiber pull’ is within acceptable limits.

- All test data shall be recorded and composed into a test report and shall be submitted to the airport / owner for approval.

- Commissioning of the system shall not begin until all test reports have been submitted and approved.

### Contractor Wireless Communication Equipment Installation  <Remove if not used>

- The antenna and lightning protection shall be provided by the manufacturer.

- The antenna mast shall be provided and installed by the electrical contractor.

- The supply, installation and termination of the interconnecting cable (between the antenna and wireless communication equipment) and associated equipment including connectors and couplings shall be the responsibility of the electrical contractor.

- The Contractor shall install and terminate and all wireless communication equipment required for the project.  This includes all of the following components:

- Antenna(s)

- Antenna mast(s)

- RF cable

- RF connectors

- Antenna Lightning arrestors

- Ground connections

- Wireless Communication Module (Mounted in Tower near Antenna)

- CAT 5 Ethernet cable (Run between wireless communication module and Tower computer)

- Installation of the wireless communication equipment shall be done by a trained and qualified RF specialist.

- The qualifications of the company and specialist to install the wireless communication equipment shall be submitted to the airport / owner for approval.

- All associated RF equipment including antennas and RF cables shall be tested upon completion of the cable installation and termination of connectors.

- The tests shall include an impedance check of the RF cable and a VSWR (Virtual Standing Wave Ratio) test.

- All test data shall be recorded and composed into a test report and shall be submitted to the airport / owner for approval.

- Commissioning of the system shall not begin until all test reports have been submitted and approved by the manufacturer.

### Contractor Hard-wire Data Cable Installation  <Remove if not used>

- The Contractor shall install, terminate and test all hard-wire communications required for the project.  This includes all of the following components:

- ALCMS manufacturer specified data cable

- Data cable termination panels

- Data cable jumper cables

- Connectors / couplings

- Junction Boxes

- Installation of the data cable shall be done by a trained and qualified specialist.

- All associated cabling, splices, jumper cable shall be tested upon completion of the cable installation and termination of connectors.

- Tests shall include verification that the ‘dB loss versus the distance of the cable pull’ is within acceptable limits.

- All test data shall be recorded and composed into a test report and shall be submitted to the airport / owner for approval.

- Commissioning of the system shall not begin until all test reports have been submitted and approved.

## Contractor Power-up and Initial Testing

- The Contractor shall perform the following power-up and commissioning tasks:

- Connect all communication equipment between Tower and Vault PLC assemblies.

- Power up Vault and Tower PLC assemblies.

- Verify communication is established between Tower and Vault PLC assemblies.

- Initiate lighting commands from Tower L-821 or Touchscreen and verify proper control operations are being executed at the Vault PLC.

- Test monitoring feedback to verify proper wiring and operation.

- Inform ALCMS manufacturer in writing all mentioned power up tests are complete.

## ALCS Manufacturer PLC Commissioning

- The ALCMS manufacturer shall perform the following commissioning tasks:

- Verify Contractor connections including power, control and monitoring.

- Verify proper labeling of equipment.

- Verify communication connections.

- Perform training on PLC control system.

- System Readiness Check

- Assist Contractor with performing the System Acceptance Testing (SAT).

## System Acceptance Test (SAT)

- Following the final installation and commissioning of the system, the ALCMS manufacturer shall perform a demonstration of the system performance.  This demonstration shall include the following:

- Lighting control functions

- Monitoring functions

- Alarm functions

- The ALCMS manufacturer shall develop a SAT test plan in accordance with the specifications.

- The SAT shall be witnessed by owner representatives, the contractor and the engineer.

## Manuals

- The ALCMS manufacturer shall provide four (4) hard copies of the operation and maintenance manuals that are hard-covered and suitable for daily operation and maintenance of the system. The manuals shall include the following information:

- Operational overview and system description

- Graphical User Interface Screen operation

- System Block Diagram

- Detailed external wiring diagrams (Electrical Contractor wiring)

- Detailed input/output terminal diagrams

- Detailed assembly drawings and wiring diagrams

- Original Equipment Manufacturer (OEM) Manuals

- The manuals shall be spiral bound or supplied in 3-ring binders.  The cover of each binder shall be labeled with all project-related information.

## As-Installed Drawings

- The ALCMS manufacturer shall provide four (4) hard copies of As-Installed drawings after system acceptance.  The As-Installed drawings shall include the following information:

- System Block Diagram (1-line drawings)

- System External Wiring Diagrams

- Assembly Drawings

- Assembly Wiring Diagrams

- The As-Installed drawings shall be 11” X 17” in size and shall be spiral bound or supplied in 3-ring binders.  The cover of each binder shall be labeled with all project-related information.

## On-site Training

- The ALCMS manufacturer shall provide to the contractor a final training course syllabus and training schedule thirty (30) days before on-site training.

- Any audio/video recordings of training classes described herein are the sole responsibility of the contractor.  Coordination of the video recording must be organized by the Contractor and approved by the engineer.

- All training sessions shall be held in a facility provided by the airport.  This facility should have tables, chairs, projection screen and sufficient space to lay out manuals and drawings.  The ALCMS Manufacturer shall provide all required visual aids and projectors.

- The ALCMS manufacturer shall provide all required visual aids and projectors.

### Air Traffic Controller Training

- The ALCMS manufacturer shall provide two (2), 1 hour User Training Class for Air Traffic Control (ATC) personnel.

- ATC Training coordinator should be present for both classes and shall be the responsible for training remaining personnel not able to attend these classes.

- This training shall include discussion and review of the following:

- PLC General System Overview

- Touchscreen Operations

- Using the Control System (GUI)

- Command and Control Sequences

- Alarm and Warning Messages

- Failsafe Conditions

- Granting Local Control to the Vaults

- Training classes for ATC personnel should be limited to a maximum of 4-6 people per class.

- Air Traffic Control should designate a training coordinator that shall be responsible for scheduling and organizing on-site training for their personnel.  In addition, this coordinator shall be responsible for training other personnel that were absent or unable to attend the training sessions.

- Any additional training beyond contract requirements shall be the responsibility of the ATC training coordinator to complete.

### Maintenance Training

- The ALCMS manufacturer shall provide one (1), 8 hour (one day) training class for maintenance personnel.  This training shall include discussion and review of the following:

- System Block Diagram

- System Assemblies and Wiring Diagrams

- Touchscreen Operation

- Graphical User Interface (GUI) Screens

- Maintenance and Troubleshooting

- Granting Local Control to the Vaults

- Power Up and Power Down Sequences

- Failsafe Operations

- Implementing Airfield Lighting Changes

- Maintenance Report Generation

- Training classes for maintenance personnel should be limited to a maximum of 4-6 people per class.

- Maintenance should designate a training coordinator that shall be responsible for scheduling and organizing on-site training for their personnel.  In addition, this coordinator shall be responsible for training other personnel that were absent or unable to attend the training sessions.

- Any additional training beyond contract requirements shall be the responsibility of the training coordinator to complete.

## Owner System Acceptance and Warranty Start Date

- Upon successful completion of the SAT and on-site training the owner shall issue the ALCMS manufacturer a written notice of system acceptance within five (5) working days.

- The date the final acceptance letter is received or five (5) days following successful completion of the SAT (whichever occurs first) represents the start of the warranty period.  Please refer to the Warranty section for more information regarding the PLC warranty guarantee.

## System Warranty

- All equipment shall be warranted against defects in workmanship, hardware and software for a period of twelve (12) months from the date of final system acceptance.

- During this time period the ALCMS manufacturer shall provide all parts, labor and technical support with the following conditions:

- The manufacturer shall correct by repair or replacement, at its option, equipment or parts which fail because of mechanical, electrical or physical defects, provided that the goods have been properly handled and stored prior to installation, properly installed and properly operated after installation, provided further that Buyer gives manufacturer written notice of such defects after delivery of the goods to Buyer.

- The manufacturer may examine any goods upon which a claim is made in the same condition as when defect therein is discovered, and may require the return of the goods to establish any claim.

- The manufacturer's liability under no circumstances shall exceed the contract price of goods claimed to be defective.

- Any returns under this guarantee are to be on a transportation charges prepaid basis.  For products not manufactured by, but sold by the manufacturer, warranty is limited to that extended by the original manufacturer.

## System Service and Support

- The ALCMS manufacturer shall provide technical assistance and support during the warranty period.

- The ALCMS manufacturer shall provide 7 days a week / 24 hours a day support phone line.

- The ALCMS manufacturer shall provide technical phone support within four (4) hours of the initial call.

- The ALCMS manufacturer shall provide free phone consultation and technical support as required during the warranty period and if necessary shall be on-site within 24 hours.

- At the request of the airport/owner, the ALCMS manufacturer shall provide information about preventative maintenance programs and extended warranty packages.

## Spare Parts Package

<<Choose Option A below if spares parts are a deliverable for the project.  Choose Option B if only a recommended spare parts package and pricing is required.  This must be determined by engineer depending on project budget>>

- A spare parts package shall be delivered as part of the system and included as part of the bid to the contractor.

- A recommended spare parts list shall be included with the Submittal including part numbers and pricing. These prices shall be valid for (12) months from date of system acceptance.

- The spare parts package shall be included with the Submittal including part numbers and parts description of what is provided.

- At a minimum, the following spare parts list or <spare parts package> shall be included as part of the project:

| Qty | Part Number | Description |
| --- | --- | --- |
| 1 |  | Touchscreen Panel Computer |
| 1 |  | PLC CPU Module |
| 1 |  | PLC Output Module |
| 1 |  | PLC Input Module |
| 1 |  | Watchdog Timer Module |
| 1 |  | Power Supply |
| 1 |  | Fiber Optic Transceiver <depends on communication type> |
| 1 |  | Wireless Radio <depends on communication type> |
| 2 |  | Current Sensing Relay <depends on monitoring requirements> |

# Equipment and Materials

## General

- The PLC system shall be based on industrial standard commercially off-the-shelf PLC components.

- The PLC equipment shall be ADB SAFEGATE or approved equivalent.

- An Ethernet (T10/100) communication network shall be used for data transfer between the electrical vault(s) and control tower.

- All touchscreen panel computers shall use flash hard drive technology and store all airport specific custom programs on Compact Flash (CF) for easy service replacement.  Refer to section 2.5 for specifications on the touchscreen panel computer(s).

- The PLC system shall be comprised of the following major hardware components:

- <Indicate Quantity> Touchscreen control station(s) located in the tower cab.

- Tower PLC subsystem consisting of an industrial enclosure, industrial PLC equipment and communication equipment.

- <Indicate Number of Vaults> Vault PLC subsystem consisting of a Touchscreen control station (installed in door of enclosure), a NEMA 12 industrial enclosure, industrial PLC equipment and communication equipment installed in Vault PLC enclosure.

- <Remove Optional equipment if not needed> Maintenance Center Touchscreen control station consisting of a Touchscreen control station (installed on a desk with desk stand) and communication equipment installed in NEMA 12 enclosure for inside wall mounting.

## Communication Network

- The tower and electrical vault(s) shall communicate with each other via one or two of the following communication networks.

<Engineer must determine type and quantity of communication needed. Typical design is one (1) fiber optic communication links.  Distances need to be determined and fiber type must be selected.  Possible options are shown below>

### Fiber Optic, 860nm, multi-mode, [maximum distance 3km]  <Remove if not used>

- Supply, installation, termination and testing of the fiber optic cable and associated equipment including fiber cable, fiber patch panels, fiber patch cables, BFOC connectors and couplings shall be the responsibility of the electrical contractor.

- The fiber optic cables shall be multi-mode, 860nm wavelength, 62.5/125 micron fiber cable.  Each fiber communication link requires 2 fibers.

- All fiber optic cable shall be terminated at a fiber optic patch panel within each subsystem before being terminated at the communication equipment.

- Fiber optic jumper cables shall be provided from the fiber patch panel to the computer equipment enclosures.

- Fiber optic cable shall be terminated with BFOC style connectors at the fiber optic transceivers located within the vault computer cabinet.

- Fiber optic runs shall not exceed 3km.  For longer distances, please contact the ALCMS manufacturer.

- Fiber optic runs shall be direct point-point runs with no splices when possible.

- Fifty percent (50%) spare fiber cables shall be pulled and terminated within the fiber optic patch panel for future expansion.

- Upon completion of fiber optic installation, the contractor shall provide airport/owner with a test report which shall include dB loss test results.

### Fiber Optic, 1310nm, single mode, [maximum distance 10km]  <Remove if not used>

- Supply, installation, termination and testing of the fiber optic cable and associated equipment including fiber cable, fiber patch panels, fiber patch cables, BFOC connectors and couplings shall be the responsibility of the electrical contractor.

- The fiber optic cables shall be single mode, 1310nm wavelength, 10/125 micron fiber cable.  Each fiber communication link requires 2 fibers.

- All fiber optic cable shall be terminated at a fiber optic patch panel within each subsystem before being terminated at the communication equipment.

- Fiber optic jumper cables shall be provided from the fiber patch panel to the computer equipment enclosures.

- Fiber optic cable shall be terminated with BFOC style connectors at the fiber optic transceivers located within the vault computer cabinet.

- Fiber optic runs shall not exceed 10km.  For longer distances, please contact the ALCMS manufacturer.

- Fiber optic runs shall be direct point-point runs with no splices when possible.

- Fifty percent (50%) spare fiber cables shall be pulled and terminated within the fiber optic patch panel for future expansion.

- Upon completion of fiber optic installation, the contractor shall provide airport/owner with a test report which shall include dB loss test results.

### Wireless Ethernet  <Remove if not used>

- The antenna shall be provided by the ALCMS manufacturer.

- The antenna mast shall be provided and installed by the electrical contractor.

- The supply, installation and termination of the interconnecting cable (between the antenna and wireless communication equipment) and associated equipment including connectors and couplings shall be the responsibility of the electrical contractor.

- The wireless network shall use direct sequencing, spread spectrum radios.

- The wireless Ethernet network shall use the 2.4 GHz ISM band and allow license-free operation.

- If the airport / owner has not previously performed a site inspection and survey and indicated an exact frequency, the ALCMS manufacturer shall provide wireless equipment that has six (6) selectable sub-channels at the following frequencies:

- Channel 1:  2.412 GHz

- Channel 2:  2.422 GHz

- Channel 3:  2.432 GHz

- Channel 4:  2.442 GHz

- Channel 5:  2.452 GHz

- Channel 6:  2.462 GHz

- The ALCMS manufacturer’s wireless communication system shall be based on direct line-of-site communication between all subsystems (unless otherwise indicated on the specification drawings).

- No repeaters shall be necessary (unless otherwise indicated on the specification drawings).

- The wireless system shall combine antenna diversity and digital signal processing to assure secure, reliable wireless communication.

<Engineer must clarify whether a radio site survey is required as this will increase the cost of the PLC system.  If the engineer and airport cannot select a predetermined frequency, a site survey is required and must be specified as part of the bid.  An example of the specification is to follow and can be removed if not required>

### ALCMS manufacturer Wireless Communication Site Inspection and Survey  <Remove if not used>

- If the airport / owner has not previously performed a site survey and indicated a specific frequency to use, the ALCMS manufacturer shall be informed prior to bid that they shall coordinate the RF site inspection and survey.

- The site inspection and survey shall be performed by a trained and qualified RF specialist to determine wireless communication equipment requirements and verify open frequencies that can be used for wireless communication.

- The cost of the site inspection and survey shall be included in the ALCMS manufacturer’s price.

- The airport / owner shall be available during inspection and survey in order to coordinate locations of antennas and wireless communication equipment (if not indicated on specification drawings).

- The inspection shall include the following:

- Inspection of all locations which will require wireless communication

- Inspection of antenna installation locations

- Verification of line-of-site from each installation location

- The survey shall include the following:

- Interference testing including a frequency sweep (using a spectrum analyzer) run over a 24 hour period.

- Usable frequency report.

- If the site inspection and survey results in any of the following items.  The airport / owner will incur all costs necessary to complete a functional wireless communication network.

- Direct line-of-site communications between one or more subsystems is not possible.

- Obstructions within the direct line-of-site require larger antenna masts.

- Obstructions within the direct line-of-site require stronger/different antennas.

- RF interference at all selectable frequencies of the wireless communication equipment prevents the use of specified equipment.

## Vault Equipment

### Vault PLC Assembly

- The Vault PLC equipment

- The Vault PLC Assembly houses the Vault communication equipment as well as a PLC for control and monitoring requirements specified at the Vault.

- The PLC Assembly is to be installed by the Contractor in coordination with the airport/engineer.

- The Vault PLC shall decode all commands received from tower and transfer them to the corresponding CCR or controllable elements.

- The Vault PLC shall continuously check for proper operation of all the communication links connected to the PLC and report any alarms to the tower.

- In the event of total communication loss or PLC failure, the Vault PLC shall go to failsafe.

- Touchscreen Panel Computer <Engineer to determine if required and remove this option if not used>

- The Vault PLC enclosure shall house a touchscreen panel computer that is installed in the door and viewable from the front exterior of the enclosure.

- Refer to section 2.5 for specifications on the touchscreen panel computer.

- Uninterruptible Power System

- An uninterruptible power system (UPS) shall be provided for supporting power of the tower equipment.

- The UPS shall be capable of supplying full load power for 10 minutes after loss of main input power.

- The UPS shall be a stand-alone unit installed in the vault equipment enclosure.

- Industrial Enclosures

- A NEMA 12 industrial enclosure is provided for housing associated Vault PLC equipment.

- The enclosure is designed for indoor use to provide protection against dust, dirt, dripping water, and external condensation of non-corrosive liquids.

- The environmental conditions within the area of the enclosure installation will not exceed 122F (50C) or fall below 32F (0C).

- Installation of the vault equipment is the responsibility of the electrical contractor.  The electrical contractor with the airport and/or owner will coordinate the installation and locations of the vault equipment.

<Engineer must clarify type of failsafe.  The most cost effective failsafe is preset which only requires relays at the Vault PLC cabinet.  A latching failsafe is possible, but requires a latching failsafe kit to be installed by the contractor in each CCR.>

### Preset Failsafe Functions  <Remove if Latching Failsafe is selected>

- The PLC shall provide a self-contained failsafe feature that shall insure default operation of the airport lighting, even if the entire airport lighting control system is not functioning.

- The failsafe setting shall be manually adjustable for each CCR regardless of internal or external control voltage.

- The failsafe system shall function from the normally closed contact of a failsafe relay.

- One (1) failsafe relay shall be provided for each CCR and controlled element.

- The PLC system shall execute failsafe mode under the following conditions:

  - Loss of communication between Tower control panel and Vault PLC

  - Vault PLC failure

  - Vault PLC communication failure

- In the event of a failsafe, the CCRs shall turn on to a pre-determined brightness level.

- The pre-determined brightness level is determined by a hard-wired jumper at the Vault PLC terminal block.

- This brightness level can be manually changed by adjusting the jumper wire at the terminal block connections for the CCR.

- The ALCMS manufacturer shall set the preset failsafe to a default failsafe state which shall be the middle brightness intensity.  (Step 3 for 5 step circuits and Step 2 for 3 step circuits.)

- Failsafe shall be able to be bypassed by selecting the CCR locally to any desired brightness level.

### Latching Failsafe Functions   <Remove if Preset Failsafe is selected>

- The PLC shall provide a latching failsafe system that shall provide mechanically latching relays for holding the Constant Current Regulators to the last commanded brightness step in the event that the PLC lighting control system is not functioning.

- The ALCMS manufacturer shall provide one (1) latching failsafe kits for each CCR and controllable element in the PLC system.

- The Contractor is responsible for installing the latching failsafe kits in each CCR and controllable element according to the ALCMS manufacturer recommendations.

- The PLC system shall execute latching failsafe mode under the following failsafe conditions:

  - Loss of communication between Tower control panel and Vault PLC

  - Vault PLC failure

  - Vault PLC communication failure

- In the event of a failsafe condition, the CCRs shall stay commanded on to the last commanded brightness level from the PLC system.  i.e. If the CCR was commanded to Step 3, it shall remain at brightness step 3.  If the CCR was commanded OFF, it shall remain OFF.

- Failsafe shall be able to be bypassed by selecting the CCR locally to any desired brightness level.

### CCR Control

- The Vault PLC shall provide a terminal block strip for connection of all control wires.

- A separate control cable shall be pulled to each Constant Current Regulator (CCR) for controlling the brightness steps of the CCR.

- The PLC system provides soft start ramping of the CCRs via a 50ms delay between each brightness step change.

- The control cable should be a multi-color cable and terminated identical for each CCR.

- Refer to Table 1.  The Vault PLC Assembly provides the following control points

### <Table shown as example only and should be updated by the engineer to reflect actual airport circuits and operation>

| Circuit ID | Description | PLC Outputs | Function |
| --- | --- | --- | --- |
| CCR 1 | Rwy 21 Edge | Dry-contact outputs | Brightness Step 1 - 5 |
| CCR 2 | Rwy 3 Edge | Dry-contact outputs | Brightness Step 1 - 5 |
| CCR 3 | Rwy 21 Approach | Dry-contact outputs | Brightness Step 1 - 5 |
| CCR 4 | Rwy 3-21 Threshold | Dry-contact outputs | Brightness Step 1 - 5 |
| CCR 5 | Taxiway Edge 1 | Dry-contact outputs | Brightness Step 1 - 3 |
| CCR 6 | Taxiway Edge 2 | Dry-contact outputs | Brightness Step 1 - 3 |
| CCR 7 | Taxiway Signs | Dry-contact outputs | Brightness Step 1 - 3 |
| Contactor 1 | Windcone | Dry-contact output | ON/OFF |
| Contactor 2 | Obstruction Lights | Dry-contact output | ON/OFF |
| Contactor 3 | Rwy 3 REIL | Dry-contact output | ON/OFF |
| Contactor 4 | Beacon | Dry-contact output | ON/OFF |

- Table 1:  Vault Control Points

### <The engineer must determine what level of monitoring is preferred by the airport and specify.  The amount of monitoring specified should be based on available budget and airport requirements.  Examples of monitoring specifications are to follow and can be removed if not required>

### Current Sensing Relay Monitoring  <Remove if no monitoring is required>

- The Vault PLC shall provide a terminal block strip for connection of all monitoring wires.

- A separate monitoring cable shall be pulled to each Constant Current Regulator (CCR) for monitoring.

- The PLC shall provide full simple ON and OFF monitoring of the CCR and other controllable elements.

- The PLC shall include the required inputs to monitor the ON/OFF status.

- A current sensing relay shall be provided for each CCR and controllable element to detect that current is detected in the output circuit.

- The CSR shall be installed in the equipment or adjacent to the equipment by the electrical contractor.

- The Contractor shall provide any additional enclosures, electrical boxes required to interface the CSR to the controlled element.

- The CSR shall be designed to provide a feedback signal to the PLC Assembly when current flow is detected on the output circuit.

- The CSR is factory set for 2.5 Amps for CCRs.

- When monitoring other equipment (i.e. contactors, relays) the CSR will have to be adjusted by the Contractor to provide appropriate feedback when the equipment is on.

- The CSR requires a minimum of 1 Amps current draw in order to activate its feedback signal.  If the equipment does not provide a minimum of 1Amp, a more sensitive CSR will have to be used.

- Refer to Table 2.  The Vault PLC Assembly provides the following monitoring points

### <Table shown as example only and should be updated by the engineer to reflect actual airport circuits and operation>

| Circuit ID | Description | PLC Input | Function |
| --- | --- | --- | --- |
| CCR 1 | Rwy 21 Edge | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 2 | Rwy 3 Edge | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 3 | Rwy 21 Approach | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 4 | Rwy 3-21 Threshold | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 5 | Taxiway Edge 1 | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 6 | Taxiway Edge 2 | 24VDC Digital Input | >2.5 Amps detected on circuit |
| CCR 7 | Taxiway Signs | 24VDC Digital Input | >2.5 Amps detected on circuit |
| Contactor 1 | Windcone | 24VDC Digital Input | >1 Amps detected on circuit |
| Contactor 2 | Obstruction Lights | 24VDC Digital Input | >1 Amp detected on circuit |
| Contactor 3 | Rwy 3 REIL | 24VDC Digital Input | >1 Amp detected on circuit |
| Contactor 4 | Beacon | 24VDC Digital Input | >1 Amp detected on circuit |

- Table 2:  Vault Monitoring Points

### CCR Remote/Local and Loss of Primary Power Status  <Remove if no monitoring is required>

- The Vault PLC shall provide a terminal block strip for connection of all monitoring wires.

- A separate monitoring cable shall be pulled to each Constant Current Regulator (CCR) for monitoring remote/local and primary power.

- The CCR must be equipped to provide one (1) dry-contact closures for remote/local signal.  CCR in Remote contact shall be closed.

- The PLC shall include one (1) input for each device to monitor Remote/Local status.

Important Note:  The contractor is responsible for assuring this contact point is available or modifies the CCR as required to provide this feedback signal.  If the signal is not available this status point will not be monitored.

- The CCR must be equipped to provide one (1) dry-contact closures for loss of primary power signal.  When CCR has primary power, the Loss of P/P contact shall be closed.

- The PLC shall include one (1) input for each device to monitor Loss of Primary Power status.

Important Note:  The contractor is responsible for assuring this contact point is available or modifies the CCR as required to provide this feedback signal.  If the signal is not available this status point will not be monitored.

## Tower Equipment

### Tower Equipment [Touchscreen and PLC Assembly]

- Touchscreen Panel PC

- The Tower Touchscreen Panel shall be installed in the new Air Traffic Control Tower in the ATC console.

- Installation is to be completed by the Contractor in coordination with ATC Technical Services.

- The installation should match existing console construction and will be of professional quality with no holes or gaps around the touchscreen.  This will be coordinated through ATC Technical Services.

- The Contractor is responsible for any additional shelves, outlets etc. to provide a clean and professional installation under the Tower cab console.

- The Contractor shall provide and terminate all wiring between the touchscreen and the Tower PLC assembly.

- A minimum of four (4) inch clearance must be provided around the perimeter of the touchscreen installation to allow for proper heat dissipation.

- Tower PLC Assembly

- The Tower PLC Assembly houses the communication equipment as well as a PLC for control and monitoring requirements specified at the Tower.

- The Tower PLC Assembly is to be installed by the Contractor in coordination with ATC Technical Services.

- The distance between touchscreen and Tower PLC assembly shall not exceed 100m (300 feet).

- The Contractor shall provide and terminate all power, wiring and communication cabling at the Tower PLC assembly.

- Uninterruptible Power System

- An uninterruptible power system (UPS) is provided for supporting power of the tower PLC equipment.

- The UPS is capable of supplying full load power for 10 minutes after loss of main input power.

- The UPS is a free standing unit.

- The contractor will supply a standard SJO cable with plug that will connect between the UPS output and the PLC enclosure Power Supply.

- Enclosures

- A NEMA 12 industrial enclosure is provided for housing associated tower PLC equipment.

- The enclosure is designed for indoor use to provide protection against dust, dirt, dripping water, and external condensation of non-corrosive liquids.

- The environmental conditions within the area of the enclosure installation will not exceed 122F (50C) or fall below 32F (0C).

- Installation of the tower equipment is the responsibility of the electrical contractor.  The electrical contractor with the airport and/or owner will coordinate the installation and locations of the tower equipment.

## Touchscreen Panel Computer

### Touchscreen

- All the touchscreen panel computers for the entire PLC system shall be industrial-grade and have the following technical specifications:

|  | Options | Description |
| --- | --- | --- |
| a. | Type | TFT XGA LCD Touchscreen Panel Computer |
| b. | Processor Type | Pentium® 4 - 2GHz minimum |
| c. | Memory Capacity | 2GByte RAM minimum |
| d. | Features | 1 X RS232, 1 X USB 1 X Ethernet (RJ45) Built-in PCMCIA Type II x 2 One PCI expansion slot |
| e. | Hard Disk See details to follow | 128GByte Solid State Flash Drive Standard rotating drives are not acceptable |
| f. | Compact Flash See details to follow | 16GByte Compact Flash Card Stores compressed “Ghost” image of Flash Drive, airport specific programs and configurations |
| g. | Touchscreen | Analog Resistive |
| h. | Size | 15” or 17” <Need to specify size> |
| i. | Resolution | 1024 X 768 minimum |
| j. | Operating System | MS Windows™ 7 |

- Table 3:  Touchscreen Panel Computer Specifications

### Flash Drive

- The computer shall use a solid state Flash Drive (no moving parts) and it shall be a Samsung or approved equal.

- The Flash Drive shall have a minimum of storage capacity of 128GB SSD.

- The Flash Drive shall operate at temperatures from 0 degrees C to +70 degrees C

- The Flash Drive shall have 1000G operating shock and 15G operating vibration rating.

- The drive shall have a MTBF of greater than 1,000,000 hours.

- The Flash Drive shall have a manufacture warranty of 3 years.

- The Flash Drive shall store the operating system and any programs that require erase/read/write cycles.

- Flash Drive specification sheets shall be provided with Submittal showing proposed flash drive meets specification requirements.

### Compact Flash Card

- The computer shall use an external Compact Flash (CF) Card which shall be installed using either a PCMCIA Compact Flash Card Reader or an external 5 ¼” bay with a compact flash card reader.

- The CF Card shall be a minimum of 16 GBytes

- No erase and/or write cycles shall occur to the Compact Flash Card.

- The CF Card shall store programs and configuration files that are only read during power-up.  These files should be the airport specific programs and configurations.

- The CF Card shall contain “Ghost” image (Exact image of the original drive) of the Flash Drive which allows for easy Flash Drive replacement and repair.

### Flash Drive Service / Repair

- The touchscreen computer shall be able to be rebuilt using a new blank Flash Drive or blank standard Hard Drive.

- The computer shall be able to boot from the CF Card and execute a “Ghost” image rebuild program.

- The rebuild program shall extract and copy the “Ghost” image, all configurations and airport specific programs from the CF Card to the new blank Flash Drive.

- Upon completion of the rebuild program, the touchscreen computer shall be able to be rebooted and be completely operational.

# Man-Machine Interface Operation

## General

- The Tower Touchscreen display shall control and monitor the airfield lighting system.  The display shall show real-time information on the operational status of the airfield lighting systems.

- The Touchscreen control stations shall consist of multiple Touchscreen ‘pages’ each with a specific function.  These Touchscreen ‘pages’ are defined as follows:

- Runway Lights: Consists of runway control touch buttons used to individually control runway circuits.  Multiple runway pages may be necessary for airports with several runways.

- Taxiway Lights: Consists of taxiway control touch buttons used to individually control taxiway circuits if required.

- Utilities: Consists of miscellaneous functions for calibrating the Touchscreen, granting lighting control to other locations, setting the date and time, etc.

- All control configurations shall be defined by the airport/owner in conjunction with Air Traffic Control requirements.

## Overview of Operation

- Airfield lighting control commands are entered into the system by touching the corresponding touch button on the Touchscreen video display.

- When a command is entered, the Touchscreen shall respond by graphically displaying the button as being depressed and change the button color.

- Once confirmed, the Tower Touchscreen shall register the command, generate a data instruction and transmit the command to the vault PLC for implementation.

- The tower Touchscreen shall receive confirmation from the vault PLC that the corresponding equipment has responded to the control command and displays the current system status on the Touchscreen display.

- In the event that communications is lost between the tower and vault(s), an alarm is indicated at each computer location.

- In the event of a predefined alarm condition, the effected airfield lighting circuit graphic shall change to red and to alert operators of the alarm condition.

### Circuit Alarms  <Remove if no monitoring is required>

- The PLC shall continuously monitor the status of all of the circuits per the monitoring requirements as specified previously.

- Any discrepancies in the monitoring (i.e. no current detected), an alarm shall be generated at the Touchscreen display for the associated circuit.

## Touchscreen Command Sequences

- The Touchscreen control station shall allow the airfield lighting circuits to be controlled individually (i.e. RWY Edge) or as a group based on preset tables.

- Each control command shall require two distinct operator actions in order for the command to initiate any state changes of the airfield lighting.  The command sequence shall be as follows:

- Select circuit: Operator selects the desired circuit to be changed.

- Select intensity: Operator selects the desired brightness step that the circuit is to be changed to.

- Graphics

- : The graphics associated with the selected circuit shall begin to flash visually indicating to the operator the airfield lighting section that is going to be affected by the command.

- Confirm/Reject: Operator selects the ‘CONFIRM’ button to accept the selection and initiate the lighting change.  Operator selects the ‘REJECT’ button to cancel the selections and make another selection.

## Touchscreen Control Methodology

<Engineer shall confirm the control methodology that is required by the airport and complete the control methodology table.  This table should reflect all equipment to be controlled, correct names to put on buttons and number of control steps.  The following table is shown as a sample only.>

- The Touchscreen software will be programmed based on the following control methodology.

| Touchscreen Button Name | Circuit(s) to Control | Number of Control Steps |
| --- | --- | --- |
| Rwy 3-21 Edge | CCR 1 – Rwy 21 Edge CCR 2 – Rwy 3 Edge CCR 4 – 3-21 Threshold | 1-5 |
| Rwy 21 Approach | CCR 3 - Rwy 21 Approach | 1-5 |
| Twy Edge & Signs | CCR 5 - Taxiway Edge 1 CCR 6 – Taxiway Edge 2 CCR 7 – Taxiway Signs | 1-3 |
| Windcone | Contactor 1 - Windcone | 1 |
| Obst. Lights | Contactor 2 - Obstruction Lights | 1 |
| Rwy 3 REIL | Contactor 3 - Rwy 3 REIL | 1 |
| Beacon | Contactor 4 - Beacon | 1 |

- Table 4:  Touchscreen Control Methodology

## Touchscreen Graphics

- The Touchscreen shall display a graphical pictorial representation of the airport runways, taxiways and other requested airport features.

- When there is a change in a lighting system status, the appropriate detail of the graphic shall indicate the status by changing color.

- The circuit intensity display colors shall be represented as seen in the legend as follows.

- Figure 1: Brightness Step Color Legend

- The status monitoring display colors shall be represented as seen in the legend as follows.  This includes ATS monitoring, Generator monitoring and communications monitoring:

- Figure 2: Status Monitoring Color Legend

## Vault Emergency Generator Control

- The PLC shall provide control of the emergency diesel generator(s) located in the airfield lighting vault(s) from all of the control stations.

- The PLC shall provide one (1) dry-contact output point(s) at the Vault.

- The PLC shall close the output to command the generator ON and open the output to turn the generator OFF.

- Locating and wiring of the output points within the Generator equipment shall be completed by the Contractor in coordination with the airport/engineer and equipment manufacturer (if required).

## Vault Automatic Transfer Switch (ATS) and Generator Monitoring

<Before specifying monitoring the Engineer shall confirm that the new/existing equipment is capable of providing the monitoring points.  ATS and Generator equipment may require additional enunciator panels in order to provide the monitoring pick-up points>

- The PLC system shall provide the optically isolated digital inputs to monitor the following feedback points:

- Utility Available

- Utility On-line

- Generator Available

- Generator On-line

- Generator Alarm

- Locating and wiring of the monitoring points within the ATS and generator equipment shall be completed by the contractor in coordination with the airport/engineer and equipment manufacturer.

## Navigational Aid Control

<Engineer needs to consider all other equipment that is currently being controlled or needs to be controlled including Windcones, Approach Systems, REILS, VASI, PAPI, Obstruction Lights, Beacon, etc..  Engineer needs to specify whether the control points need to be at the Vault or at the Tower >

- The PLC shall provide control of the <Enter other control items here or remove if not required> from all of the control stations.

- The PLC shall provide one (1), dry-contact output point(s) at the <Specify Tower or Vault depending on how it is to be controlled.  Typically all control comes from Vault, but some equipment control exists out of the tower>.

- The PLC shall close the output to command the device ON and open the output to turn the device OFF.

- Locating and wiring of the output points within the device shall be completed by the Contractor in coordination with the airport/engineer and equipment manufacturer

<The following specification is a sample for airport’s with radio controllers which operate the lighting after hours.  This section can be removed if not required>

## Radio Control Enabled Control Methodology

- The PLC shall provide an interface to the airport’s radio control equipment.

- One (1) button labeled “Radio Control” will be programmed to allow air-to-ground radio control after normal operating hours.

- When the radio control button is pressed, all preset settings are changed for radio operations according to the preset control methodology.

- Radio Control preset lighting settings shall be specified by the airport.

### Radio Control Interface

- The PLC system will provide three (3) inputs for status monitoring of the Radio Controller at the vault from all control stations.

- The input(s) are optically isolated and require the monitoring source and common from the monitored device.

- Inputs are rated at 24-48VDC and 120-240VAC at 1 amp.

- The PLC will monitor the inputs and adjust the airfield lighting according to the Radio Control preset table.

- The PLC will only monitor for the radio control inputs when the “Radio Control” button is enabled at the Tower.

- Locating and wiring of the output points within the Radio Controller equipment shall be completed by the contractor in coordination with the airport/engineer and equipment manufacturer (if required).

### Radio Control Operations

- The PLC system shall interface to the Radio Controller and control the airfield lighting according to the table to follow.

| Touchscreen Button Name | Circuit(s) to Control | Default Step | Low (3 click) | Medium (3 click) | High (3 click) |
| --- | --- | --- | --- | --- | --- |
| Radio Control Enabled | CCR 1 – Rwy 21 Edge CCR 2 – Rwy 3 Edge CCR 3 – Rwy 21 Approach CCR 4 – 3-21 Threshold | 1 | 1 | 3 | 5 |
|  | CCR 5 - Taxiway Edge 1 CCR 6 – Taxiway Edge 2 CCR 7 – Taxiway Signs | 1 | 1 | 2 | 3 |
|  | Windcone | 1 | 1 | 1 | 1 |
|  | Contactor 3 - Rwy 3 REIL | 1 | 1 | 1 | 1 |
|  | Contactor 4 - Beacon | 1 | 1 | 1 | 1 |

- Table 5:  Touchscreen Radio Control Methodology