SAMPLE SPECIFICATION: Amerace® 54Super Kit

EQUIPMENT AND MATERIALS

- Each L-823 plug and receptacle housing shall have a metal insert molded into the rubber, which shall mate with a corresponding part of the appropriate pin or socket, to provide a permanent metal to metal connection between the housing and the pin or socket.

- Each plug and receptacle shall have a permanently molded pull over sleeve at the interface end, to be pulled over completed connections, thus providing a full seal against dirt, and a second seal against water entry. The sleeve shall be reusable for the life of the connector.

INSTALLATION

- After assembly, the connection between the connector housings (both plug and receptacle) and the cable must be capable of withstanding a static longitudinal pull test of 50 kg. This shall be confirmed by a pull test in which the connector housings shall be held or pulled in such a manner as not to impart a crimping or clamping action to the cable, and the cable shall be held or pulled from the conductor only (to prevent separation of the insulation from the remainder of the cable). A force of at least 50 kg shall be applied and then released. A change in position between a connector housing and the outside of the cable of more than 10 mm shall be cause for rejection.