Site Visit and

Development Guide

Airfield Lighting Control and

Monitoring System

ADB SAFEGATE

977 Gahanna Parkway

Columbus, Ohio 43230

Tel: 1-614-861-1304

www.adbsafegate.com

Table of Contents

1.	Job Scope and System External Guide	4

1.1	Number of Subsystems	4

1.2	Type of Communication	5

1.3	Communication Requirements Notes	5

1.4	Radio Survey Information (Skip this section if Radios are not used)	7

1.5	Equipment Locations	7

2.	Touchscreen Control Methodology	9

2.1	Miscellaneous Control and Monitoring	9

2.2	Regulator Control Methodology	10

2.3	Airport’s with Radio Control Methodology	11

2.4	Airfield Graphics Methodology	12

3.	Tower Subsystem Requirements	13

3.1	Options	13

3.2	Installation Considerations	13

3.3	Special Control or Monitoring Points Required in Tower	13

4.	Vault Subsystem Guide	14

4.1	Options	14

4.2	Failsafe	14

4.3	Installation Considerations	14

4.4	Special Control or Monitoring Points Required in Vault	14

4.5	Generator and other Miscellaneous I/O	15

5.	Constant Current Regulator Monitoring Guide	16

5.1	Monitoring Type	16

5.2	Primary Power and Remote/Local Monitoring	16

6.	Maintenance Center Subsystem Guide	18

6.1	Options	18

6.2	Installation Considerations	18

6.3	Constant Current Regulator Index	18

List of Figures

Figure 1:  Color-coded airfield circuit diagram	12

List of Tables

Table 1:  Touchscreen Button Control Methodology	10

Table 2:  RL-854 Radio Control Methodology	11

Table 3:  Primary Power / Remote Local Pick-up Points	17

Table 4:  Look-up Chart for Other Manufacturer’s	17

Table 5:  Constant Current Regulator Index <Blank>	20

Objective:  This guide will assist in the design and development of the ALCMS system.  Each section should be reviewed to verify that all details have been reviewed.  Details regarding this project may be located in the engineering drawings or specifications.  A site visit may be required if the information is not indicated in the plans and specifications.

Preparation Checklist:

  	Schedule Site Visit: Make sure all required personnel will be available at the site.  This includes Airport Designer, Airport Maintenance, FAA/ATC and Sales person.

  	Tool kit with RMS Meter, current clamp, and leads.

  	Copies of airport designer plans and specifications to verify accuracy on site.

  	Copy of preliminary ADB SAFEGATE Submittal if completed to verify accuracy on site.

  	List of specific questions and concerns after review of plans and specifications.

# Job Scope and System External Guide

Airport name:

Project Number:

Project Description:

## Number of Subsystems

Description						Quantity

	Touchscreen Control Stations		_____

Size of Touchscreen(s): _______

	Tower		_____

	Maintenance Center		_____

	Operations		_____

	Vault(s) (list descriptions below i.e. East Vault)	_____

Vault 1: ________________________________________

Vault 2: ________________________________________

Vault 3: ________________________________________

	Other: _________________________________________

  - Type of Communication

Description	Type	Description	Number of Links	Distance

Tower to Vault(s):	 Hard-wired	#Cond/AWG ____	_____	_____

 Fiber Optics	Size/Mode_____	_____ 	_____

 Wireless Radio	Frequency_____	_____ 	_____

 Other:____________ 			_____	_____

Pick One:

  Tower to Maintenance(s):	 Hard-wired	#Cond/AWG ____	_____	_____

  Vault to Maintenance(s):	 Fiber Optics	Size/Mode_____	_____  	_____

 Wireless Radio	Frequency_____	_____ 	_____

  Other:____________ 			_____	_____

Other comm. link(s):	 Hard-wired	#Cond/AWG ____	_____	_____

_________________ to	 Fiber Optics	Size/Mode_____	_____  	_____

_________________	 Wireless Radio	Frequency_____	_____ 	_____

 Other:____________ 			_____	_____

  - Communication Requirements Notes

Confirm Communication meets the following requirements

Dial-up links not recommended for modes of communication except Remote dial-in capabilities.

Fiber Optic Ethernet, Multi-mode

100BASE-T [maximum distance 2km / 6,600 feet]

- The fiber optic cables shall be multi-mode, 1300nm wavelength, 62.5/125 micron fiber cable.  Each fiber communication link requires 2 fibers.

- All fiber optic cable shall be terminated at a fiber optic patch panel within each subsystem before being terminated at the communication equipment.

- Fiber optic jumper cables shall be provided from the fiber patch panel to the computer equipment enclosures.

- Fiber optic cable shall be terminated with ST style connectors at the fiber optic transceivers located within the vault computer cabinet.

- Fiber optic runs shall be direct point-point runs with no splices if installation allows.

- Fifty percent (50%) spare fiber cables shall be pulled and terminated within the fiber optic patch panel for future expansion.

- Upon completion of fiber optic installation, the airport/owner should receive a test report which should include dB loss test results.

Fiber Optic Ethernet, Single mode

100BASE-T [maximum distance 20km / 65,600 feet]

- The fiber optic cables shall be single mode, 1300nm wavelength, 8/125 micron fiber cable.  Each fiber communication link requires 2 fibers.

- All fiber optic cable shall be terminated at a fiber optic patch panel within each subsystem before being terminated at the communication equipment.

- Fiber optic jumper cables shall be provided from the fiber patch panel to the computer equipment enclosures.

- Fiber optic cable shall be terminated with ST style connectors at the fiber optic transceivers located within the vault computer cabinet.

- Fiber optic runs shall be direct point-point runs with no splices if installation allows.

- Fifty percent (50%) spare fiber cables shall be pulled and terminated within the fiber optic patch panel for future expansion.

- Upon completion of fiber optic installation, the airport/owner should receive a test report which should include dB loss test results.

Hard-wire, Serial Communication

19,200 baud rate [maximum distance 1.6km / 5280 feet]

9600 baud rate [maximum distance 3.2km / 10,560 feet]

- The hard wire cable shall be stranded copper, twisted pair conductors, 20 AWG, 600V rated.  Each hard wire communication link requires 2 twisted pair or 4 total conductors.

- All cable shall be terminated at a terminal cabinet within each subsystem before being terminated at the communication equipment.

- Cable jumpers shall be provided from the terminal cabinet to the computer equipment enclosures.

- Hard wire runs shall be direct point-point runs with no splices if installation allows.

- Fifty percent (50%) spare conductors shall be pulled and terminated within the terminal cabinet for future expansion.

- Upon completion of hard wire installation, the airport/owner should receive a continuity and resistance test report that confirms proper installation.

Wireless Ethernet [Requires Direct line-of-site]

2Mbps, 11dB Antenna Gains [maximum distance .5km / 1600 feet]

2Mbps, 18dB Antenna Gains [maximum distance 2.5km / 8200 feet]

2Mbps, 24dB Antenna Gains [maximum distance 10km / 32,800 feet]

- The wireless network shall use direct sequencing, spread spectrum radios.

- The wireless Ethernet network shall use the 2.4 GHz ISM band and allow license-free operation.

- If the airport / owner has not previously performed a site inspection and survey and indicated an exact frequency, the Designer shall perform radio site survey and select wireless frequency.  Typical wireless equipment provides selectable frequency sub-channels that the Designer must verify that these frequencies are not used at the airport or by local business, police stations, fire departments and government offices.  An example of the frequency sub-channels are as follows:

Channel 1:  2.412 GHz

Channel 2:  2.422 GHz

Channel 3:  2.432 GHz

Channel 4:  2.442 GHz

Channel 5:  2.452 GHz

Channel 6:  2.462 GHz

- The Designer shall verify wireless communication system has direct line-of-site between subsystems.  No obstructions including trees, buildings, towers etc. can be between locations of antennas.

- The wireless system shall combine antenna diversity and digital signal processing to assure secure, reliable wireless communication.

  - Radio Survey Information (Skip this section if Radios are not used)

Wireless Communication Site Inspection

As part of selecting the use of wireless communication, the Airport Designer shall have complete an on-site inspection and survey which includes the following:

- A RF site inspection and survey shall be performed by a trained and qualified RF specialist to determine wireless communication equipment requirements and verify open frequencies that can be used for wireless communication.

- The Designer in cooperation with the airport / owner shall have previously determined antenna installation locations and mast sizes.  All of these locations shall be indicated on the specification drawings.

- The Designer shall have previously verified that direct line-of-site communication is possible between all locations.

- If direct line-of-site is not possible, locations of all repeaters must be specified.

- Line-of-site distances between all locations shall be specified.

- The Designer should have completed an interference test that includes a frequency sweep (using a spectrum analyzer) run over a 24 hour period.  The resulting usable frequency report should be included as part of the design.

Frequencies in use:		1.)_________________			2.)_________________

3.)_________________			4.)_________________

Continue on another sheet if necessary

Radio description	Transmitter model:	_________________

Frequency to use (pick one): 	Channel 1:  2.412 GHz    Channel 2:  2.422 GHz

Channel 3:  2.432 GHz    Channel 4:  2.442 GHz

Channel 5:  2.452 GHz    Channel 6:  2.462 GHz

Tower description	Height:	_________________

Number of floors:	_________________

Antenna Mast limitations: 	_________________

Grounding Locations for mast: 	_________________

Distance from Antenna to radio: 	_________________

Antenna style: 	  Parabolic    Patch     Omni

Vault description	Height: 	_________________

Number of floors:	_________________

Antenna Mast limitations: 	_________________

Grounding Locations for mast: 	_________________

Distance from Antenna to radio: 	_________________

Antenna style: 	  Parabolic    Patch     Omni

Maintenance Center

(if required)	Height: 	_________________

Number of floors:	_________________

Antenna Mast limitations: 	_________________

Grounding Locations for mast: 	_________________

Distance from Antenna to radio: 	_________________

Antenna style: 	  Parabolic    Patch     Omni

  - Equipment Locations

Touchscreen							Location Specified (Room/Floor)

Touchscreen							______________________________________

Dimensions of console:	Width:	__________

Height:	__________

Depth:	__________

  Video Extension Equipment / Audible Alarm			______________________________________

	Take a picture of panel location for records.

	Verify that the console location is sufficient for specified touchscreen.

	Inspect location for obstructions that may affect panel depth.

	Inspect location to verify that proper ventilation is available.

Tower								Location Specified (Room/Floor)

Tower Computer Enclosure: (i.e. Tower equipment room, 9th floor)	______________________________________

  Fiber Patch Panel (supplied by others)				______________________________________

  Hard-wire terminal cabinet (supplied by others)			______________________________________

  Radio Antenna						______________________________________

Vault								Location Specified (Room/Floor)

Vault Computer Enclosure: (i.e. Tower equipment room, 9th floor)	______________________________________

  Fiber Patch Panel (supplied by others)				______________________________________

  Hard-wire terminal cabinet (supplied by others)			______________________________________

  Radio Antenna						______________________________________

Maintenance Center						Location Specified (Room/Floor)

Maintenance Computer: (i.e. Supervisor’s office)			______________________________________

  Fiber Patch Panel (supplied by others)				______________________________________

  Hard-wire terminal cabinet (supplied by others)			______________________________________

  Radio Antenna						______________________________________

Other node (please specify):					Location Specified (Room/Floor)

Remote Viewing Computer: (i.e. Operations Center)			______________________________________

  Fiber Patch Panel (supplied by others)				______________________________________

  Hard-wire terminal cabinet (supplied by others)			______________________________________

  Radio Antenna						______________________________________

- Touchscreen Control Methodology

This section reviews what equipment needs to be controlled by the Touchscreen.  This is important to develop the touchscreen software.

## Miscellaneous Control and Monitoring

  It is important to take a look at the existing control panel / L-821 while on-site.

  Take pictures of old L-821 for reference when laying out new touchscreen design

  Approach System Control (Specify approaches and modes i.e. ALSF/SSALR, Strobes etc.)

  PAPI Control	(Specify direction and control i.e. ON/OFF, intensity control etc.)

  Generator Control and Feedback

  Generator ON/OFF		  Generator Alarm		  Generator On-line

  Generator Running		  Vault Utility Available 		  Vault Utility On-line

  Other:________________

  System Control Group:

  Beacon				  Windcone       		  Crash,Fire and Rescue

  Obstruction Light		  Wig Wag        		  Holding Lights

  Other:________________

  System and Communications Status Feedback:

  Communication Status	(i.e.  COMM1 failure)

  Control Status   		(i.e. Vault Control, Tower Control)

  Other:_____________________________

  Runway Visual Range Feedback (RVR):

  Contact closures for Steps 3, 4 and 5

List circuits to monitor RVR:

1.) ____________________________________

2.) ____________________________________

3.) ____________________________________

4.) ____________________________________

  Land and Hold Short Lights:

List Power Control Units (PCU) and LAHSO text on button (i.e. RWY 18 LAHSO):

1.) ____________________________________

2.) ____________________________________

3.) ____________________________________

4.) ____________________________________

## Regulator Control Methodology

Please complete Table 1 that will describe the control methodology between the Touchscreen and the Vault Regulators.  This table will describe all of the Touchscreen buttons and indicate which Regulator(s) in the Vault will be controlled by the button.

This control methodology is programmed and is not field adjustable.  It is important that the information in this table is thoroughly reviewed for accuracy.  See example to determine information required.

|  | Preset Button Y/N |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ID |  | Touchscreen Page | Circuit Button | Circuit Elements | Circuit Steps See Note 1 |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 13 |  |  |  |  |  |
| 14 |  |  |  |  |  |
| 15 |  |  |  |  |  |
| 16 |  |  |  |  |  |
| 17 |  |  |  |  |  |
| 18 |  |  |  |  |  |
| 19 |  |  |  |  |  |
| 20 |  |  |  |  |  |
| 21 |  |  |  |  |  |
| 22 |  |  |  |  |  |
| 23 |  |  |  |  |  |
| 24 |  |  |  |  |  |
| 25 |  |  |  |  |  |

Table 1:  Touchscreen Button Control Methodology

Note 1:  Circuit Steps indicates how many control steps the circuit has.  Some regulators may have multiple steps, but are controlled differently

For example:  	A Sign circuit may use a 3 step CCR, but is typically controlled as 1 step CCR at step 2, 5.5A

A PAPI circuit may use a 3 step CCR, but only be controlled as ON/OFF, Step 3, 6.6

A REIL circuit may use a 3 step CCR, but only be controlled as ON/OFF, Step 3, 6.6

## Airport’s with Radio Control Methodology

	RL-854 Radio Controller (If checked list requirements in table).  Type:____________________________

Note: Control Industries requires 3 capacitors (low, med. High) to be cut to signal to ground and control.

See example filled out in the table for reference.

ADB SAFEGATE Safegate provides three (3) isolated inputs for monitoring the RL-854 radio and waits for the Low, Medium and High contact closures from the RL-854.

|  |  |  | Rwy 18-36 Radio Control #1 |  |  |  |  | Rwy XXX Radio Control #2 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CIRCUIT |  | Enabled |  |  |  |  | Enabled |  |  |  |
| ID | DESCRIPTIONS | Steps | Default | Low (3 Click) | Med (5 Click) | High (7 Click) |  | Default | Low (3 Click) | Med (5 Click) | High (7 Click) |
| 1 | Rwy Edge 1 | 5 | 1 | 1 | 3 | 5 |  | NA | NA | NA | NA |
| 2 | Rwy Edge 2 | 5 | 1 | 1 | 3 | 5 |  | NA | NA | NA | NA |
| 3 | Twy A | 3 | 0 | 1 | 2 | 3 |  | NA | NA | NA | NA |
| 4 | Twy B | 3 | 0 | 1 | 2 | 3 |  | NA | NA | NA | NA |
| 5 | Twy C | 3 | 0 | 1 | 2 | 3 |  | NA | NA | NA | NA |
| 6 | PAPI | 3 | 1 | 1 | 2 | 3 |  | NA | NA | NA | NA |
| 7 | Beacon | 1 | 1 | 1 | 1 | 1 |  | NA | NA | NA | NA |
| 8 |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  |  |  |  |

Table 2:  RL-854 Radio Control Methodology

## Airfield Graphics Methodology

 	Obtain color-coded copy of the airport’s airfield circuit layout including runways, taxiways, apron lights, approaches, REILS, PAPIS, VASIS etc.  Color-coded circuit layout example shown in Figure 1.

  	Obtain electronic copy of the airport’s airfield circuit layout in AutoCAD release 12 or higher.

Figure 1:  Color-coded airfield circuit diagram

- Tower Subsystem Requirements

## Options

Number of Computers: ___________

Processor type and speed:____________(i.e. Pentium III 750MHz)

  Desktop / Commercial Computer

  Industrial Computer

  3.5” Floppy Disk Drive

  Single Hard Drive		Hard Drive size:___________(i.e. 10G)

  Dual Mirrored Hard Drives	Hard Drive size:___________(i.e. 10G)

  CD R/W ROM

  UPS Backup				Backup time required:_______________

  Air Conditioning required by specification (temperature >100)

  Heater required by specification (temperature < 32)

  Other: ___________________________________

  Other: ___________________________________

## Installation Considerations

  Take a picture of tower enclosure location for records.

  Verify that the location is sufficient for specified enclosure.

  Inspect doorway entrances and height that may affect installation.

  Inspect location to verify that proper ventilation is available.

## Special Control or Monitoring Points Required in Tower

	RVR monitoring (If checked list associated circuits)

ADB SAFEGATE provides dry-contact closure for steps 3,4 and 5 only.  3 points per circuit.

Associated circuits:	1.)  _________________________	4.)  ____________________________

2.)  _________________________	5.)  ____________________________

3.)  _________________________	6.)  ____________________________

	Beacon Control (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for Beacon.

	Maintain contact closure      	Pulse output (Specify delay).

	Crash, Fire and Rescue (Air Rescue and Fire Fighters/ ARFF) (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for ARFF.

	Maintain contact closure      	Pulse output (Specify delay).

	RL-854 Radio Controller (If checked list requirements).

ADB SAFEGATE provides isolated input to read radio inputs.

	Other Equipment Control or Monitoring (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for Miscellaneous Equipment.

Other:_____________________________________

Other:_____________________________________

Other:_____________________________________

- Vault Subsystem Guide

## Options

Number of Computers: ___________

Processor type and speed:____________(i.e. Pentium III 750MHz)

  Desktop / Commercial Computer

  Industrial Computer

  3.5” Floppy Disk Drive

  Single Hard Drive		Hard Drive size:___________(i.e. 10G)

  Dual Mirrored Hard Drives	Hard Drive size:___________(i.e. 10G)

  CD R/W ROM

  UPS Backup			Backup time required:_______________

  Printer				Type required:_______________

  Air Conditioning required by specification (temperature >100)

  Heater required by specification (temperature < 32)

  Other: ______________________________________________

## Failsafe

  Latching (Circuits stay at last commanded step during failure)

  Preset (Circuits change to a pre-determined setting)  NOT RECOMMENDED

## Installation Considerations

  Take a picture of vault enclosure location for records.

  Verify that the location is sufficient for specified enclosure.

  Inspect doorway entrances and height that may affect installation.

  Inspect location to verify that proper ventilation is available.

## Special Control or Monitoring Points Required in Vault

	RVR monitoring (If checked list associated circuits)

ADB SAFEGATE provides dry-contact closure for steps 3,4 and 5 only.  3 points per circuit.

Associated circuits:	1.)  _________________________	4.)  ____________________________

2.)  _________________________	5.)  ____________________________

3.)  _________________________	6.)  ____________________________

	Beacon Control (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for Beacon.

	Maintain contact closure 		Pulse output (Specify delay).

	Crash, Fire and Rescue (Air Rescue and Fire Fighters/ ARFF) (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for ARFF.

	Maintain contact closure 		Pulse output (Specify delay).

	Other Equipment Control or Monitoring (If checked list requirements).

ADB SAFEGATE provides dry-contact closure for Miscellaneous Equipment.

Other:_____________________________________

Other:_____________________________________

## Generator and other Miscellaneous I/O

ADB SAFEGATE provides dry-contact closure only for any of the following controlled points

  Windcone

  Obstruction Light

  Wig Wag

  Crossing Lights

  Strobes

  Other:_______________________

  Other:_______________________

  Generator Control

Generator Requirements:			  Pulse Signal		Pulse duration:_______

  Contact closure	Contact rating:________

  Separate contact closure for START and STOP

- Constant Current Regulator Monitoring Guide

## Monitoring Type

	Take a picture of locations were Monitoring components will be installed.  This includes Current Sensing Relay boxes, Distributed monitoring boxes etc.

	Verify that there are no space limitations where components will be located.  i.e. no height limitations for installation of enclosures.

  	No Monitoring

  	L-827 Monitoring (Distributed Monitoring)

Number of Circuits ______

L-827 Mounting requirements:	  At ADB SAFEGATE’s discretion

  Boxes mounted on walls

  CVM mounted in each CCR

  Boxes mounted on uni-strut racks

  	Current Sensing Monitoring (On/Off Monitoring)

Number of Circuits ______

Current Sensing requirements:	  At ADB SAFEGATE’s discretion

  CSR boxes mounted on walls

  CSR installed in each CCR

 	Insulation Resistance Monitoring

Number of Circuits ______

IRMS Mounting requirements:	  At ADB SAFEGATE’s discretion

  Boxes mounted on walls

  IRM mounted in each CCR

  Boxes mounted on uni-strut racks

## Primary Power and Remote/Local Monitoring

In order to monitor primary power and remote local it is important to determine ahead of time what locations in each regulator the contractor will wire to in order for ADB SAFEGATE to monitor these points.  Many newer regulators do not default with these monitoring points and require modification kits provided by others.  Here is how the primary power and remote local must work.

	Obtain Regulator Manufacturer’s Manuals and schematics.

	Determine Regulator’s Internal Feedback Contacts for Modification Kits.  Use Table 3 to follow to record pick-up point information if CCR does not match one described in Table 4.

| Monitoring Point | Monitoring Action |
| --- | --- |
| Primary Power | Contact must close when input Primary Power is available. Contact must open when input Primary Power is turned off. Contact must not be affected by the Remote/Local switch. |
| Internal Remote | Contact must close when Regulator is in Remote. Contact must open when in any Local step or Off. |

| Regulator Description / Part Number | Feedback Description | Regulator Internal Contact Points |
| --- | --- | --- |
|  | Primary Power |  |
|  | Remote / Local |  |
|  | Primary Power |  |
|  | Remote / Local |  |

Table 3:  Primary Power / Remote Local Pick-up Points

| Regulator Description Part Number | Feedback Description | Regulator Internal Contact Points | Comments |
| --- | --- | --- | --- |
| Crouse-Hinds Pull-out drawer type | Primary Power | CCI (120VAC) Neutral (N) or L1 (Pri. Pwr Contactor Leg 1) L2 (Pri. Pwr Contactor Leg 2) | Check with meter |
| # 31060 series i.e. 31060-50-P-11-CM | Remote / Local | Requires S446 Install Kit (C-H) TB1 71 (N) TB1 72 (120VAC) | Most require this kit Some work if hooked up here, check with meter and switch the R/L switch |
| Crouse-Hinds Keypad type | Primary Power | CCI (120VAC) Neutral (N) | Check with meter |
| 82860 series i.e. 82860-D-20-9-66-05 | Remote / Local | Requires Option 23 Kit (C-H) | Will not work w/o kit |
| Crouse-Hinds Rotary switch type | Primary Power | CCI (120VAC) Neutral (N) | Check with meter |
| 82860 series i.e. 82860-D-20-9-66-05 | Remote / Local | Requires S446 Install Kit (C-H) | Will not work w/o kit |
| Crouse-Hinds Old oil-filled w/ white cap on top | Primary Power | XCP (120VAC) N (N) | Check with meter |
|  | Remote / Local | CCI (120VAC) N (N) | Check with meter |
| Hevi-Duty | Primary Power | FU1 (120VAC Fuse holder) N (N) | Check with meter |
| Large Gray CCR | Remote / Local | CCI (120VAC) N (N) | Check with meter |

Table 4:  Look-up Chart for Other Manufacturer’s

- Maintenance Center Subsystem Guide

## Options

Number of Computers: ___________

Processor type and speed:____________(i.e. Pentium III 750MHz)

  Desktop / Commercial Computer

  Industrial Computer

  3.5” Floppy Disk Drive

  Single Hard Drive		Hard Drive size:___________(i.e. 1.2G)

  Dual Mirrored Hard Drives	Hard Drive size:___________(i.e. 1.2G)

  CD ROM

  CD R/W ROM

  Zip Drive

  Modem			Speed required:_______________

  UPS Backup				Backup time required:_______________

  Printer				Type required:_______________

  Air Conditioning required by specification (temperature >100)

  Heater required by specification (temperature < 32)

  Other: ___________________________________

  Other: ___________________________________

## Installation Considerations

  Take a picture of maintenance center location for records.

  Verify that the location is sufficient for specified computer equipment.

  Inspect doorway entrances and height that may affect installation.

  Inspect location to verify that proper ventilation is available.

## Constant Current Regulator Index

Please complete Table 5 and include all Regulators being controlled at the Vault.  This information is needed in order to correctly specify and design the Vault control equipment.  See the first example in the table to understand information required.

Get Latest Version of CCR Index from Product Center on website

THIS PAGE INTENTIONALLY LEFT BLANK

FOR DUPLEX PRINTING

| CCR # | ACE # | ACE Configuration | COM Ch 1 | COM Ch 2 | CCR Name Line 1 | CCR Name Line 2 | kW | Internal CCI Voltage | Output Current | Lamps Out | Manufacturer and Model | Input Monitoring | Output Monitoring | BRITE Master # | Remote Count | ACE Integrated | Circuit Selector Name (See Note 1) | Loop 1 | Loop 2 | Loop 3 | Loop 4 | Input Voltage |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 |  | 1001 | 2001 | Runway | 18-36 Edhe 1 | 30 | 120VAC | 6.6 | Yea | Siemens CCF123-234 | No | Yes |  |  | Yes |  |  |  |  |  | 480VAC |
| 2 | 2 |  | 1002 | 2002 | Taxiway | A Edge | 15 | 120VAC | 6.6 | Yes | Crouse-Hinds 66000 | No | Yes |  |  | No |  |  |  |  |  | 480VAC |
| 3 | 3 |  | 1003 | 2003 | Taxiway | E and C Edge | 30 | 120VAC | 6.6 | Yes | Siemens CCF30-120 | No | Yes |  |  | Yes | CSS #1 E&C Edge | E Edge | C Edge |  |  | 480VAC |
| 4 | 4 |  | 1004 | 2004 | Stopbar | B1 and B2 | 20 | 120VAC | 6.6 | Yes | Siemens CCF20-120 | No | Yes | 1 | 120 | Yes |  |  |  |  |  | 480VAC |

Note 1: Airport must inform whether circuit selector is to operate as Exclusive [only 1 loop on at a time because CCR size or airport operations} or Accumulative [1 or both loops can be on at a time, CCR can support both circuits]

Table 5:  Constant Current Regulator Index <Blank>