Items in italic are to be finalized by the airport.

ITEM L-150  INSTALLATION OF LED IN-PAVEMENT UTILITY LIGHT FIXTURES

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing LED in-pavement utility light fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the light fixtures in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  LED IN-PAVEMENT FIXTURE.  The LED in-pavement utility light (IUL) fixture shall be manufactured according to the applicable requirements of an L-852T fixture as defined in FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures” and FAA “Engineering Brief No. 67” (current edition).  The LED in-pavement utility light fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

{If required by the airport authority, a Return on Investment (ROI) and Life Cycle Cost (LCC) analysis shall be calculated to validate the benefit of the LED fixture in comparison to the equivalent incandescent technology.}

150-2.2  EQUIPMENT SUPPLIED.  LED IUL fixtures shall be supplied for the total quantity as shown on the plans.  Each lot shipment of fixtures shall include one Instruction Manual.  The manufacturer shall also have a downloadable electronic version of the manual available on their web site.

The IUL fixture light source shall be a Light Emitting Diode assembly.  The average lifetime of the LED shall be 100,000 hours.  The color emitted by the fixture shall be {White} {Yellow} {Green} {Blue}.  The required color shall be obtained without the use of a color filter.

The LED IUL fixture shall be FAA Style 3 (( ¼ inch above grade).  The top cover shall be of single piece construction and made from an aluminum alloy to enhance fixture strength.  All components shall be corrosion proof without the use of environmentally hazardous metal protective coatings, such as cadmium plating.  The fixture glass lens shall be field replaceable without the use of epoxy or other sealing compounds and shall be held in place by means of a mechanical clamping device.  Grommets, in conjunction with a mechanical clamping device, shall be used for the entry and sealing of the FAA L-823 male cord set wire cables to the bottom cover.  This will allow for cord set replacement without the use of epoxy or other sealing compounds.  To ensure the wire entry is waterproof, a FAA L-823 secondary female connector kit shall be used for the electrical connection during installation.  A test port with removable plug shall be provided in the bottom cover to allow for pressure testing after fixture overhaul.  To insure fixture quality, the manufacturer shall production leak and insulation resistance test each individual fixture prior to shipment.  The leak test shall be by means of a Helium tank testing apparatus, capable of detecting minor fixture leaks.

150-2.3  FIXTURE POWER.  {The LED IUL fixture, without heater, shall be powered from a direct voltage source of 95VAC (minimum) to 264VAC (maximum), 50/60 Hz.  The LED IUL fixture load shall be14.3VA maximum.  The LED IUL fixture light output shall stay constant throughout the input voltage range of 95Vac to 264Vac.}  {The LED IUL fixture, with heater, shall be powered from a direct voltage source of ±120Vac, 50/60 Hz.  The LED IUL fixture load shall be38VA maximum.  The LED IUL fixture light output shall stay constant throughout the input voltage range of ±120Vac, 50/60 Hz.}  The fixture bottom cover shall include an earth ground terminal.

150-2.4  FIXTURE MOUNTING.  The LED IUL fixture shall be a {FAA standard 12-inch diameter fixture using 6 evenly spaced bolts on an 11.25 inch bolt-circle.  The fixture shall be designed to mount on a FAA L-868 base can}  {FAA standard 12-inch diameter fixture using 6 evenly spaced bolts on a 10.25 inch bolt-circle.  The fixture shall be designed to mount on a FAA L-867 base can}  {8-inch diameter fixture using 2 bolts spaced 180 degrees apart on a 7.32 inch bolt-circle.  The fixture shall be designed to mount on an 8-inch FAA style light base can}.

CONSTRUCTION METHODS

150-3.1  PLACING THE LED IUL FIXTURE.  The contractor shall furnish and install each LED in-pavement utility light fixture as specified in the proposal and shown in the plans.  The LED IUL fixtures shall be mounted on industry standard FAA {L-868} {L-867} {8-inch light base} cans as specified and shown by location on the plans.

150-3.2  TESTS. The LED IUL fixtures shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance. The test shall include turning the power source on and off not less than 10 times at the beginning and end of the 24-hour test. The LED IUL fixtures shall illuminate properly during each portion of the test.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for {TBD} LED in-pavement utility light fixtures, and one Instruction Manual (per lot) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of LED in-pavement utility light fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	LED in-pavement utility light fixtures, in Place—per each

END OF ITEM L-150