L-852G LED RUNWAY GUARD LIGHT FIXTURE - SAMPLE SPECIFICATION

Note: Modify the items in italics according to your specific job requirements.

ITEM L-150   INSTALLATION OF LED L-852G IN-PAVEMENT FIXTURES

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing the LED L-852G Runway Guard Light (RGL) in-pavement fixtures in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the fixtures in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  IN-PAVEMENT FIXTURE.  The LED L-852G in-pavement fixtures shall conform to the requirements of FAA Advisory Circular 150/5345-46 (current edition) “Specification for Runway and Taxiway Light Fixtures” and FAA LED “Engineering Brief No. 67” (current edition).  The fixtures shall be ETL certified and listed in AC 150/5345-53 (current edition), Appendix 3 at the time of bid.  {The fixture shall also comply with ICAO Annex 14, Vol. 1, par. 5.3.22, Configuration B.}  {The LED L-852G Style 2, without heater, shall also comply with CE requirements as specified in EMC Directive 2004/108/EC.} The in-pavement fixtures shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

{If required by the airport authority, a Return on Investment (ROI) and Life Cycle Cost (LCC) analysis shall be calculated to validate the benefit of the LED fixture in comparison to the equivalent incandescent technology.}

150-2.2  EQUIPMENT SUPPLIED.  A quantity of {TBD} in-pavement fixtures shall be supplied.  Each lot shipment shall include one Instruction Manual.  The manufacturer shall also have a downloadable electronic version of the manual available on their web site.

150-2.3  L-852G FIXTURE.  To insure reduced energy, taxiway down time and maintenance requirements, the L-852G in-pavement fixture shall utilize a Light Emitting Diode (LED) light source.  The average lifetime of any LED within the fixture shall be greater than 50,000 hours.  The color emitted by the fixture shall be uni-directional Traffic Signal yellow.  The required color shall be obtained without the use of a color filter.  It shall be possible to install the LED fixtures on existing series circuits in replacement of conventional quartz-incandescent lights without having to change the CCR, series circuit primary wiring or isolation transformer.

The L-852G fixture shall be Style 2 ( ½ inch above grade).  The L-852G top cover shall be of single piece, 12” construction (2-piece top covers will not be allowed) and made from an aluminum alloy to enhance fixture strength.  All components shall be corrosion proof without the use of environmentally hazardous metal protective coatings, such as cadmium plating.  The prism shall be field replaceable without the use of epoxy or other sealing compounds and held in place by means of a mechanical clamping device.  Grommets, in conjunction with a mechanical clamping device, shall be used for the entry and sealing of L-823 cord set wire cable to the inner cover.  This will allow for cord set replacement without the use of epoxy or other sealing compounds.  A test port with removable plug will be provided in the bottom cover to allow for pressure testing after fixture overhaul.  To insure fixture quality, the manufacturer will production leak and dielectric strength test each individual fixture prior to shipment.  The leak test will be by means of a Helium tank testing apparatus, capable of detecting minor fixture leaks due to material porosity.

150-2.4  FIXTURE ELECTRONICS.  The light fixture shall operate on either a 2.8A to 6.6A or 8.5A to 20A circuit at 60Hz {50Hz} using an appropriately-sized isolation transformer. To minimize spare parts requirements, the fixture internal power supply circuit shall be the same for 3-step or 5-step, 50/60Hz series circuits.

For a Style 3 fixture, an option for a heater shall be available that complies with the arctic kit requirements in Engineering Brief No.67 (current edition).  To reduce overall energy consumption, the heater shall be thermostatically controlled.

{The fixture will be used in a non-electronically monitored application.  The fixture shall be connected directly to an isolation transformer.  The fixture load shall be no more than 75VA (without a heater) and use a 65W, 6.6A (secondary) isolation transformer and shall be no more than 93VA (with a heater) and use a 100W, 6.6A (secondary) isolation transformer.  Both the fixture input maximum VA load and the maximum CCR load shall be shown on the catalog sheet included with the submittal documents.  Pulsing synchronization of the fixture shall be accomplished using on-board electronics.  It shall be possible to order a fixture with a factory set Initial ON and Initial OFF setting.  A Remote Control device shall be supplied with each lot of fixtures that will allow maintenance to easily modify the Initial flash ON or OFF fixture setting.}

{The fixture will be used in an electronically monitored application.  The fixture shall be connected to a Local Control Device according to the manufacturer’s recommendations.  Pulsing synchronization of the fixture shall be accomplished using output current On/Off activation from the Local Control Device.  The fixture load shall be no more than 96VA (without a heater) and use a 150W, 6.6A (secondary) isolation transformer and shall be no more than 120VA (with a heater) using a 150W, 6.6A (secondary) isolation transformer.  Both the fixture input maximum VA load and the maximum CCR load shall be shown on the catalog sheet included with the submittal documents.}

“Smart electronics” shall control current to LED, so that the light output matches existing incandescent fixtures at all brightness levels without sacrificing any light characteristics.  To insure reduced risk of inadvertent light output switching, the actual light output shall be determined based on a continuous light output curve and not separate discrete steps.  This insures light output truly represents input current, even if series circuit input current is not within FAA specification limits.  To reduce risk of inadvertent light output variation (such as when a series circuit fault is occurring), the fixture electronics shall incorporate a time delay before switching to a new light output setting.

The fixture bottom cover shall include an earth ground terminal.

CONSTRUCTION METHODS

150-3.1  PLACING THE IN-PAVEMENT FIXTURES.  The contractor shall furnish and install each in-pavement fixture as specified in the proposal and shown in the plans.  Each in-pavement fixture shall be mounted on the appropriate base can at the location shown on the plans.

150-3.2  TESTS.  Each fixture shall be connected to the series circuit using the manufacturer’s recommended isolation transformer {and, for monitored applications, the manufacturer’s recommended power line carrier device}.  The constant current regulator (CCR) shall then be tested to verify the correct output current is present at each step.  The output current shall be checked using the CCR manufacturer’s instructions using a True RMS meter.  The entire circuit shall then be fully tested by continuous operation for not less than 24 hours prior to acceptance.  At the end of 8 consecutive hours, the lights shall be visually checked for proper synchronization.  The 24 hours operation test shall include operating the (CCR) in each step (Local and Remote) not less than 10 times at the beginning and end of the 24-hour period.

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of equipment to be paid for under this item shall be for {TBD} LED L-852G in-pavement fixtures, and one Instruction Manual (per lot) installed and accepted as a completed unit, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed total quantity of in-pavement fixtures installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1  LED L-852G in-pavement fixtures, in Place—per each

END OF ITEM L-150