## SGRS Requirements
Switchgear Regulator System SGRS
Requirements Gathering Worksheet
Project Number: | [14 empty] | Reference: SGRS Load Worksheet
Airport Name: | [14 empty] | Version: v.3.0
Configuration options for the Switchgear Regulator System
Please enter the configuration using the drop down menu of each selection box. Additional comments can be entered in the corresponding boxes.
SGRS TYPE
REGULATOR TYPE |  | NOTES: | [8 empty] | SGRS TYPE NOTES:
Ferro (CSF)
POWERPACK TYPE |  | Removable Powerpack Ferro only
Removable Powerpack |  | CCT Thyristor Stackable only
ENCLOSURE RATING
Non-Siesmic <STANDARD> |  | Non-Siesmic is STANDARD
BUSS CURRENT RATING
600 |  | 600A is STANDARD
INPUT VOLTAGE
480V, Delta |  | 480V, Delta is STANDARD
INCOMING POWER BAY OPTIONS
INPUT CURRENT PROTECTION | [10 empty] | INCOMING POWER BAY NOTES:
None - External circuit breaker <STANDARD>
INPUT VOLTAGE PROTECTION
None - External protection <STANDARD>
INCOMING DIGITAL METER
None <STANDARD>
NUMBER OF COPPER BUSSES
Single Buss <STANDARD>
POWERPACK OPTIONS
BRIGHTNESS CONTROL |  | DOOR INDICATOR STATUS POINTS | [12 empty] | POWERPACK NOTES:
ACE II <STANDARD>
|  | No <STANDARD> | [5 empty] | DOOR OPEN
INPUT MONITORING
None <STANDARD> |  | No <STANDARD> | [5 empty] | FAN RUNNING
OUTPUT MONITORING |  | No <STANDARD> | [5 empty] | OVER TEMPERATURE
None
OTHER OPTIONS
IRMS MONITORING
None <STANDARD> |  | No <STANDARD> | [5 empty] | DIGITAL POWER METER
S1 SERIES CIRCUIT CUTOUT |  | No <STANDARD> | [5 empty] | OPERATIONS COUNTER
None <STANDARD>
|  | No <STANDARD> | [5 empty] | ELAPSE TIME METER
SGRS LINEUP CONFIGURATIONS
CCR SIZE
|  | Output | 2.5 | 4 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 50 | 70 |  | Buss Current: | 600
LINEUP #1 <Indicate Lineup name below> |  | 6.6A | [12 empty] | Buss Voltage: | 480
|  | 20A | [12 empty] | Utility Transformer: | Delta
|  | Total Powerpacks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Avail. Current: | 1039.2305
|  | Current draw each | 11.8313 | 11.8313 | 22.1836 | 22.1836 | 29.5782 | 42.0322 | 56.0429 | 82.2368 | 82.2368 | 135.5876 | 187.8033 | Total | Loading %
|  | Total Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | Must be less than 100%
CCR SIZE
|  | Output | 2.5 | 4 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 50 | 70 |  | Buss Current: | 600
LINEUP #2 <Indicate Lineup name below> |  | 6.6A | [12 empty] | Buss Voltage: | 480
|  | 20A | [12 empty] | Utility Transformer: | Delta
|  | Total Powerpacks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Avail. Current: | 1039.2305
|  | Current draw each | 11.8313 | 11.8313 | 22.1836 | 22.1836 | 29.5782 | 42.0322 | 56.0429 | 82.2368 | 82.2368 | 135.5876 | 187.8033 | Total | Loading %
|  | Total Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | Must be less than 100%
CCR SIZE
|  | Output | 2.5 | 4 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 50 | 70 |  | Buss Current: | 600
LINEUP #3 <Indicate Lineup name below> |  | 6.6A | [12 empty] | Buss Voltage: | 480
|  | 20A | [12 empty] | Utility Transformer: | Delta
|  | Total Powerpacks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Avail. Current: | 1039.2305
|  | Current draw each | 11.8313 | 11.8313 | 22.1836 | 22.1836 | 29.5782 | 42.0322 | 56.0429 | 82.2368 | 82.2368 | 135.5876 | 187.8033 | Total | Loading %
|  | Total Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | Must be less than 100%
CCR SIZE
|  | Output | 2.5 | 4 | 5 | 7.5 | 10 | 15 | 20 | 25 | 30 | 50 | 70 |  | Buss Current: | 600
LINEUP #4 <Indicate Lineup name below> |  | 6.6A | [12 empty] | Buss Voltage: | 480
|  | 20A | [12 empty] | Utility Transformer: | Delta
|  | Total Powerpacks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Avail. Current: | 1039.2305
|  | Current draw each | 11.8313 | 11.8313 | 22.1836 | 22.1836 | 29.5782 | 42.0322 | 56.0429 | 82.2368 | 82.2368 | 135.5876 | 187.8033 | Total | Loading %
|  | Total Current | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | Must be less than 100%
OTHER OPTIONS
S1 SERIES CIRCUIT CUTOUT BAY |  | POWERPACK LIFT | [11 empty] | OTHER COMMENTS:
No <STANDARD> |  | No <STANDARD>
CONTROL INTERFACE BAY |  | POWER PACK STORAGE DOCK
No <STANDARD> |  | No <STANDARD>
MONITORING INTERFACE BAY |  | HOUSEKEEPING PAD MUST NOT EXCEED
No <STANDARD> |  | 4 INCHES HIGH
SPARE PARTS, TRAINING AND TESTING
COMMENTS:
PLEASE REVIEW OR STANDARD SERVICES WILL BE PROVIDED
SPARE PARTS REQUIRED
No <STANDARD>
FACTORY ACCEPTANCE TEST
Non-witnessed FAT | Days: | 0
MAINTENANCE TRAINING
Standard Training - Specify hours / days | Hours: | 16 hours / 2 days / 1 trip | [8 empty] | Number of People |  | 0
INSTALLATION SERVICES
Standard Installation Services and SAT | Hours:
-SGRS Worksheet-
Type
Ferro (CCF/CHF)
Ferro (CSF)
CCT (Thyristor Controlled)
Powerpack Types
Removable Powerpack
Stackable (Not removable)
Enclosure Ratings
Non-Siesmic <STANDARD>
Seismic Zone 4
No. of Busses
Single Buss <STANDARD>
Double Buss - Upper/Lower
Buss Current
600
800
Input Voltage
480V, Delta | 1
480V, Wye | 2
600V, Delta <Canada>
600V, Wye <Canada> | 3
Current Protection
None - External circuit breaker <STANDARD>
Circuit Breaker
Fuseable disconnect
Voltage Protection
None - External protection <STANDARD>
TVSS - Transient Voltage Surge Protection
Incoming Power Meter
None <STANDARD>
3 Phase Meter with CT's
3 Phase Meter with CT's and alarm contacts
Utility Transformer Type
Delta
Wye
Control Option
ACE II <STANDARD>
ACE
DCMU
Hard-wired
Output Monitoring Option
None
Current Sensing Relays (CSR)
Current / Voltage (CVM)
Digital Power Meter Only
IRMS Option
No <STANDARD>
IRMS Monitoring
Input Monitoring Option
None <STANDARD>
Input Current / Voltage (CVM)
S1 CUTOUT IN POWERPACK
No <STANDARD>
Yes - Integrated in Powerpack
Yes - Installed in S1 Enclosure
Door Indicator Status Points
No <STANDARD>
Required
S1 Enclosure
No <STANDARD>
Yes - SAS Cutouts
Yes - Other Man. Cutouts
Interface Bay
No <STANDARD>
Yes - Terminal Block for hardwire control
Yes - Terminal Blocks and CT/PT Bay
MONITORING Interface Bay
No <STANDARD>
Yes - Enclosure for other man. Equipment
Powerpack Lift
No <STANDARD>
Battery-operated lift
Hydrolic Lift - Requires 11 feet clearance
Reduced Profile Lift - Requires 7 feet clearance
Powerpack Storage Dock
No <STANDARD>
Yes - Dual Dock houses up to two 70kW
Spare Parts
No <STANDARD>
Yes - Specify in Comments
Factory Acceptance Test
Non-witnessed FAT
Witnessed FAT - ADB Pays - Specify days / people
Witnessed FAT - Customer Pays
Witnessed FAT - Contractor Pays
Training
None - Contractor to Train
Standard Training - Specify hours / days
Special Training requirements - See Comments
Training Length
None
8 hours / 1 day / 1 trip
16 hours / 2 days / 1 trip
24 hours / 3 days / 1 trip
32 hours / 4 days / 1 trip
40 hours / 5 days / 1 trip
Special - See Comments
Installation
None - Contractor to Install and Test
Standard Installation Services and SAT

## 600A Delta
Regulator size | Number |  | 1L
70's From A-B |  |  | 600A Delta
50's From A-B
30's From A-B | 1 |  | Instructions:
25's From A-B
20's From A-B |  |  | 1) Determine the numbers and sizes of the regulators to be used in the SGRS
15's From A-B |  |  | 2) Place the regulators between phase pairs attempting to place an equal load on each phase
10's From A-B |  |  | 3) Compare the currents on the individual phases and shuffle regulators to balance the loads
7.5's From A-B
5's From A-B |  |  | Notes:
4's From A-B |  |  | It gets a little complicated. However, a 600 amp buss can deliver 346 amps per phase.
2.5's From A-B
Because the phases get shared, this results in the equivelent of 1039 amps being available
70's From A-C
50's From A-C |  |  | If the load on the phases exceeds 80%, future expansion needs to be carefully considered.
30's From A-C | 1 |  | A single 30kW regulator contributes 82 amps of load to a SGRS. This is nearly 8% of the
25's From A-C |  |  | full capacity of a "600 amp" buss at 480 vac.
20's From A-C
15's From A-C |  |  | Each regulator draws current from two phases. If a regulator is on the A-B phases, it will
10's From A-C |  |  | contribute to the total current on both phase A and on phase B.
7.5's From A-C
5's From A-C |  |  | All regulator loads assume worst case allowed by AC 150/5345-10 with an additional
4's From A-C |  |  | lamps out allowance
2.5's From A-C
70's From B-C
50's From B-C
30's From B-C
25's From B-C
20's From B-C | 1
15's From B-C
10's From B-C
7.5's From B-C
5's From B-C
4's From B-C
2.5's From B-C
Number of Regulators | 3
Current on A | 142.4384 | 23.74%
Current on B | 120.4678 | 20.08%
Current on C | 120.4678 | 20.08%
Total | 220.5166 | 21.22%

## 600A Delta sht2
Misc
Max SGRS power |  | 498830.6326
Sum of single phase current |  | 1039.2305
Current phasor contributions
Regulator size |  |  |  | Magnitude | Angle | Real | Imag
70's From A-B | 0 |  |  | 0
50's From A-B | 0 |  |  | 0
30's From A-B | 1 |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
25's From A-B | 0 |  |  | 0
20's From A-B | 0 |  |  | 0
15's From A-B | 0 |  |  | 0
10's From A-B | 0 |  |  | 0
7.5's From A-B | 0 |  |  | 0
5's From A-B | 0 |  |  | 0
4's From A-B | 0 |  |  | 0
2.5's From A-B | 0 |  |  | 0
Iab |  |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
70's From A-C | 0 |  |  | 0
50's From A-C | 0 |  |  | 0
30's From A-C | 1 |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
25's From A-C | 0 |  |  | 0
20's From A-C | 0 |  |  | 0
15's From A-C | 0 |  |  | 0
10's From A-C | 0 |  |  | 0
7.5's From A-C | 0 |  |  | 0
5's From A-C | 0 |  |  | 0
4's From A-C | 0 |  |  | 0
2.5's From A-C | 0 |  |  | 0
Iac |  |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
Iac phased |  |  |  |  | -101.8051 | -16.8243 | -80.4975
70's From B-C | 0 |  |  | 0
50's From B-C | 0 |  |  | 0
30's From B-C | 0 |  |  | 0
25's From B-C | 0 |  |  | 0
20's From B-C | 1 |  |  | 56.0429 | 18.1949 | 53.2407 | 17.4994
15's From B-C | 0 |  |  | 0
10's From B-C | 0 |  |  | 0
7.5's From B-C | 0 |  |  | 0
5's From B-C | 0 |  |  | 0
4's From B-C | 0 |  |  | 0
2.5's From B-C | 0 |  |  | 0
Ibc |  |  |  | 56.0429 | 18.1949 | 53.2407 | 17.4994
Ibc phased |  |  |  |  | 138.1949 | -41.7753 | 37.3581
Individual phases
| Real | Imag | Mag | Angle | %
Ia | 94.9493 | 106.1759 | 142.4384 | 48.1949 | 0.2374
Ib | -119.9003 | 11.6797 | 120.4678 | 5.5637 | 0.20078
Ic | 24.951 | -117.8556 | 120.4678 | -78.0465 | 0.20078
Regulator size data | [7 empty] | Real | Imag | Mag | Angle | degrees | Inverse
|  |  | Voltage | Size | Efficiency | PF | Current draw | [5 empty] | Mag | angle
30 kVA |  |  | 480 | 30 | 0.92 | 0.95 | 82.2368 | 78.125 | 25.6784 | 82.2368 | 0.31756 | 18.1949 | 0.01216 | -18.1949
25 kVA |  |  | 480 | 25 | 0.9 | 0.95 | 70.0536 | 66.5509 | 21.8742 | 70.0536 | 0.31756 | 18.1949 | 0.014275 | -18.1949
20 kVA |  |  | 480 | 20 | 0.9 | 0.95 | 56.0429 | 53.2407 | 17.4994 | 56.0429 | 0.31756 | 18.1949 | 0.017843 | -18.1949
15 kVA |  |  | 480 | 15 | 0.9 | 0.95 | 42.0322 | 39.9306 | 13.1245 | 42.0322 | 0.31756 | 18.1949 | 0.023791 | -18.1949
10 kVA |  |  | 480 | 10 | 0.9 | 0.9 | 29.5782 | 26.6204 | 12.8928 | 29.5782 | 0.45103 | 25.8419 | 0.033809 | -25.8419
7.5 kVA |  |  | 480 | 7.5 | 0.9 | 0.9 | 22.1836 | 19.9653 | 9.6696 | 22.1836 | 0.45103 | 25.8419 | 0.045078 | -25.8419
5 kVA |  |  | 480 | 5 | 0.9 | 0.9 | 14.7891 | 13.3102 | 6.4464 | 14.7891 | 0.45103 | 25.8419 | 0.067617 | -25.8419
4 kVA |  |  | 480 | 4 | 0.9 | 0.9 | 11.8313 | 10.6481 | 5.1571 | 11.8313 | 0.45103 | 25.8419 | 0.084522 | -25.8419
2.5 kVA |  |  | 480 | 2.5 | 0.9 | 0.9 | 7.3945 | 6.6551 | 3.2232 | 7.3945 | 0.45103 | 25.8419 | 0.13523 | -25.8419
50 kVA |  |  | 480 | 50 | 0.93 | 0.95 | 135.5876 | 128.8082 | 42.3372 | 135.5876 | 0.31756 | 18.1949 | 0.0073753 | -18.1949
70 kVA |  |  | 480 | 70 | 0.94 | 0.95 | 187.8033 | 178.4131 | 58.6416 | 187.8033 | 0.31756 | 18.1949 | 0.0053247 | -18.1949
Lamps out factor | 1.15
Voltage | 480

## 800A Delta
Regulator size | Number |  | 1L
70's From A-B | 1 |  | 800A Delta
50's From A-B
30's From A-B |  |  | Instructions:
25's From A-B
20's From A-B |  |  | 1) Determine the numbers and sizes of the regulators to be used in the SGRS
15's From A-B |  |  | 2) Place the regulators between phase pairs attempting to place an equal load on each phase
10's From A-B |  |  | 3) Compare the currents on the individual phases and shuffle regulators to balance the loads
7.5's From A-B
5's From A-B |  |  | Notes:
4's From A-B |  |  | It gets a little complicated. However, a 800 amp buss can deliver 461 amps per phase.
2.5's From A-B
Because the phases get shared, this results in the equivelent of 1386 amps being available
70's From A-C
50's From A-C |  |  | If the load on the phases exceeds 80%, future expansion needs to be carefully considered.
30's From A-C | 1 |  | A single 30kW regulator contributes 82 amps of load to a SGRS. This is nearly 6% of the
25's From A-C |  |  | full capacity of a "800 amp" buss at 480 vac.
20's From A-C
15's From A-C |  |  | Each regulator draws current from two phases. If a regulator is on the A-B phases, it will
10's From A-C |  |  | contribute to the total current on both phase A and on phase B.
7.5's From A-C
5's From A-C |  |  | All regulator loads assume worst case allowed by AC 150/5345-10 with an additional
4's From A-C |  |  | lamps out allowance
2.5's From A-C
70's From B-C
50's From B-C
30's From B-C
25's From B-C
20's From B-C | 1
15's From B-C
10's From B-C
7.5's From B-C
5's From B-C
4's From B-C
2.5's From B-C
Number of Regulators | 3
Current on A | 239.7443 | 29.97%
Current on B | 221.2146 | 27.65%
Current on C | 120.4678 | 15.06%
Total | 326.083 | 23.53%

## 800A Delta sht2
Misc
Max SGRS power |  | 665107.5101
Sum of single phase current |  | 1385.6406
Current phasor contributions
Regulator size |  |  |  | Magnitude | Angle | Real | Imag
70's From A-B | 1 |  |  | 187.8033 | 18.1949 | 178.4131 | 58.6416
50's From A-B | 0 |  |  | 0
30's From A-B | 0 |  |  | 0
25's From A-B | 0 |  |  | 0
20's From A-B | 0 |  |  | 0
15's From A-B | 0 |  |  | 0
10's From A-B | 0 |  |  | 0
7.5's From A-B | 0 |  |  | 0
5's From A-B | 0 |  |  | 0
4's From A-B | 0 |  |  | 0
2.5's From A-B | 0 |  |  | 0
Iab |  |  |  | 187.8033 | 18.1949 | 178.4131 | 58.6416
70's From A-C | 0 |  |  | 0
50's From A-C | 0 |  |  | 0
30's From A-C | 1 |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
25's From A-C | 0 |  |  | 0
20's From A-C | 0 |  |  | 0
15's From A-C | 0 |  |  | 0
10's From A-C | 0 |  |  | 0
7.5's From A-C | 0 |  |  | 0
5's From A-C | 0 |  |  | 0
4's From A-C | 0 |  |  | 0
2.5's From A-C | 0 |  |  | 0
Iac |  |  |  | 82.2368 | 18.1949 | 78.125 | 25.6784
Iac phased |  |  |  |  | -101.8051 | -16.8243 | -80.4975
70's From B-C | 0 |  |  | 0
50's From B-C | 0 |  |  | 0
30's From B-C | 0 |  |  | 0
25's From B-C | 0 |  |  | 0
20's From B-C | 1 |  |  | 56.0429 | 18.1949 | 53.2407 | 17.4994
15's From B-C | 0 |  |  | 0
10's From B-C | 0 |  |  | 0
7.5's From B-C | 0 |  |  | 0
5's From B-C | 0 |  |  | 0
4's From B-C | 0 |  |  | 0
2.5's From B-C | 0 |  |  | 0
Ibc |  |  |  | 56.0429 | 18.1949 | 53.2407 | 17.4994
Ibc phased |  |  |  |  | 138.1949 | -41.7753 | 37.3581
Individual phases
| Real | Imag | Mag | Angle | %
Ia | 195.2374 | 139.139 | 239.7443 | 35.4762 | 0.29968
Ib | -220.1884 | -21.2834 | 221.2146 | -5.5211 | 0.27652
Ic | 24.951 | -117.8556 | 120.4678 | -78.0465 | 0.15058
Regulator size data | [7 empty] | Real | Imag | Mag | Angle | degrees | Inverse
|  |  | Voltage | Size | Efficiency | PF | Current draw | [5 empty] | Mag | angle
30 kVA |  |  | 480 | 30 | 0.92 | 0.95 | 82.2368 | 78.125 | 25.6784 | 82.2368 | 0.31756 | 18.1949 | 0.01216 | -18.1949
25 kVA |  |  | 480 | 25 | 0.9 | 0.95 | 70.0536 | 66.5509 | 21.8742 | 70.0536 | 0.31756 | 18.1949 | 0.014275 | -18.1949
20 kVA |  |  | 480 | 20 | 0.9 | 0.95 | 56.0429 | 53.2407 | 17.4994 | 56.0429 | 0.31756 | 18.1949 | 0.017843 | -18.1949
15 kVA |  |  | 480 | 15 | 0.9 | 0.95 | 42.0322 | 39.9306 | 13.1245 | 42.0322 | 0.31756 | 18.1949 | 0.023791 | -18.1949
10 kVA |  |  | 480 | 10 | 0.9 | 0.9 | 29.5782 | 26.6204 | 12.8928 | 29.5782 | 0.45103 | 25.8419 | 0.033809 | -25.8419
7.5 kVA |  |  | 480 | 7.5 | 0.9 | 0.9 | 22.1836 | 19.9653 | 9.6696 | 22.1836 | 0.45103 | 25.8419 | 0.045078 | -25.8419
5 kVA |  |  | 480 | 5 | 0.9 | 0.9 | 14.7891 | 13.3102 | 6.4464 | 14.7891 | 0.45103 | 25.8419 | 0.067617 | -25.8419
4 kVA |  |  | 480 | 4 | 0.9 | 0.9 | 11.8313 | 10.6481 | 5.1571 | 11.8313 | 0.45103 | 25.8419 | 0.084522 | -25.8419
2.5 kVA |  |  | 480 | 2.5 | 0.9 | 0.9 | 7.3945 | 6.6551 | 3.2232 | 7.3945 | 0.45103 | 25.8419 | 0.13523 | -25.8419
50 kVA |  |  | 480 | 50 | 0.93 | 0.95 | 135.5876 | 128.8082 | 42.3372 | 135.5876 | 0.31756 | 18.1949 | 0.0073753 | -18.1949
70 kVA |  |  | 480 | 70 | 0.94 | 0.95 | 187.8033 | 178.4131 | 58.6416 | 187.8033 | 0.31756 | 18.1949 | 0.0053247 | -18.1949
Lamps out factor | 1.15
Voltage | 480

## 600A Wye
Regulator size | Number
70's From A |  |  |  | Wye Connected Loads
50's From A
30's From A |  |  | Instructions:
25's From A
20's From A |  |  | 1) Determine the numbers and sizes of the regulators to be used in the SGRS
15's From A |  |  | 2) Place the regulators between phase pairs attempting to place an equal load on each phase
10's From A |  |  | 3) Compare the currents on the individual phases and shuffle regulators to balance the loads
7.5's From A
5's From A |  |  | Notes:
4's From A |  |  | It gets a little complicated. However, a 600 amp buss can deliver 600 amps per phase.
2.5's From A
Because the phases do not get shared,
70's From B |  |  | this results in the equivelent of the number of phases times the current per phase being available
50's From B
30's From B |  |  | If the load on the phases exceeds 80%, future expansion needs to be carefully considered.
25's From B |  |  | A single 30kW regulator contributes 114 amps of load to a SGRS. This is nearly 9% of the
20's From B |  |  | full capacity of a "600 amp" buss at 480 vac.
15's From B
10's From B |  |  | Each regulator draws current from only one phase
7.5's From B |  |  | If a regulator is on the A phase, it will add to that current only
5's From B
4's From B |  |  | All regulator loads assume worst case allowed by AC 150/5345-10 with an additional
2.5's From B |  |  | lamps out allowance
70's From C
50's From C
30's From C
25's From C
20's From C
15's From C
10's From C
7.5's From C
5's From C
4's From C
2.5's From C
Number of Regulators | 0
Current on A | 0 | 0%
Current on B | 0 | 0%
Current on C | 0 | 0%
Total | 0 | 0%

## 600A Wye sht2
Bus Bar Max Load | 400
Line Voltage | 347
Number of Phases | 3
Misc
Max SGRS power |  | 416400
Sum of single phase current |  | 1200
Regulator size |  |  |  | Magnitude
70's From A | 0 |  |  | 0
50's From A | 0 |  |  | 0
30's From A | 0 |  |  | 0
25's From A | 0 |  |  | 0
20's From A | 0 |  |  | 0
15's From A | 0 |  |  | 0
10's From A | 0 |  |  | 0
7.5's From A | 0 |  |  | 0
5's From A | 0 |  |  | 0
4's From A | 0 |  |  | 0
2.5's From A | 0 |  |  | 0
Ia |  |  |  | 0
70's From B | 0 |  |  | 0
50's From B | 0 |  |  | 0
30's From B | 0 |  |  | 0
25's From B | 0 |  |  | 0
20's From B | 0 |  |  | 0
15's From B | 0 |  |  | 0
10's From B | 0 |  |  | 0
7.5's From B | 0 |  |  | 0
5's From B | 0 |  |  | 0
4's From B | 0 |  |  | 0
2.5's From B | 0 |  |  | 0
Ib |  |  |  | 0
70's From C | 0 |  |  | 0
50's From C | 0 |  |  | 0
30's From C | 0 |  |  | 0
25's From C | 0 |  |  | 0
20's From C | 0 |  |  | 0
15's From C | 0 |  |  | 0
10's From C | 0 |  |  | 0
7.5's From C | 0 |  |  | 0
5's From C | 0 |  |  | 0
4's From C | 0 |  |  | 0
2.5's From C | 0 |  |  | 0
Ic |  |  |  | 0
Individual phases
Mag
Ia |  |  | 0
Ib |  |  | 0
Ic |  |  | 0
Regulator size data | [7 empty] | Real | Imag | Mag | Angle | degrees | Inverse
|  |  | Voltage | Size | Efficiency | PF | Current draw | [5 empty] | Mag | angle
30 kVA |  |  | 480 | 30 | 0.92 | 0.95 | 82.2368 | 78.125 | 25.6784 | 82.2368 | 0.31756 | 18.1949 | 0.01216 | -18.1949
25 kVA |  |  | 480 | 25 | 0.9 | 0.95 | 70.0536 | 66.5509 | 21.8742 | 70.0536 | 0.31756 | 18.1949 | 0.014275 | -18.1949
20 kVA |  |  | 480 | 20 | 0.9 | 0.95 | 56.0429 | 53.2407 | 17.4994 | 56.0429 | 0.31756 | 18.1949 | 0.017843 | -18.1949
15 kVA |  |  | 480 | 15 | 0.9 | 0.95 | 42.0322 | 39.9306 | 13.1245 | 42.0322 | 0.31756 | 18.1949 | 0.023791 | -18.1949
10 kVA |  |  | 480 | 10 | 0.9 | 0.9 | 29.5782 | 26.6204 | 12.8928 | 29.5782 | 0.45103 | 25.8419 | 0.033809 | -25.8419
7.5 kVA |  |  | 480 | 7.5 | 0.9 | 0.9 | 22.1836 | 19.9653 | 9.6696 | 22.1836 | 0.45103 | 25.8419 | 0.045078 | -25.8419
5 kVA |  |  | 480 | 5 | 0.9 | 0.9 | 14.7891 | 13.3102 | 6.4464 | 14.7891 | 0.45103 | 25.8419 | 0.067617 | -25.8419
4 kVA |  |  | 480 | 4 | 0.9 | 0.9 | 11.8313 | 10.6481 | 5.1571 | 11.8313 | 0.45103 | 25.8419 | 0.084522 | -25.8419
2.5 kVA |  |  | 480 | 2.5 | 0.9 | 0.9 | 7.3945 | 6.6551 | 3.2232 | 7.3945 | 0.45103 | 25.8419 | 0.13523 | -25.8419
50 kVA |  |  | 480 | 50 | 0.93 | 0.95 | 135.5876 | 128.8082 | 42.3372 | 135.5876 | 0.31756 | 18.1949 | 0.0073753 | -18.1949
70 kVA |  |  | 480 | 70 | 0.94 | 0.95 | 187.8033 | 178.4131 | 58.6416 | 187.8033 | 0.31756 | 18.1949 | 0.0053247 | -18.1949
Lamps out factor | 1.15
Voltage | 480

## CB Sizes
Circuit Breaker Sizes available
800 | Standard
400 | Standard
250 | Custom
225 | Custom
200 | Custom
175 | Custom
150 | Custom
125 | Custom
110 | Custom
100 | Custom