Suggested Specification: IN-OMA

- The taxiway edge inset light shall be omnidirectional medium intensity complying with ICAO recommendations in Annex 14, Volume I, paragraph 5.3.17, with FAA L-852T, STANAG 3316, CAP168 and British Standards BS 3224.

- It shall be fitted with one 6.6 Amps halogen pre-focused dichroic reflector lamps of 40 or 45 Watts. Lamp life shall be at full intensity greater than 1,500 hours.

- All external parts shall be made of anodized tempered aluminum alloy casting.

- All fixings and fastenings shall be stainless steel.

- It shall have a maximum outer diameter of 203 mm (8”) and its projection shall not exceed 10 mm (<1/2”).

- It must be able to be installed directly on an 8” shallow base, or by means of adapter on a FAA L-868B deep base or a seating ring.

- It will be designed to allow for easy maintenance.

- The prisms shall not be sealed.

- The filters shall be dichroic.

- The fittings in this range share many of the same components.

- No internal adjustment shall be needed.

- The weight of the fitting shall be less than 3 kg.