## L-850A LED wo Heater
| ADB SAFEGATE L-850A LED without Heater High Intensity Runway Centerline Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 150
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For uni-directional LED, use 20/25W. For uni-directional Qtz or bi-directional LED (with one cordset), use 30/45W. For bi-directional Qtz with 2 cordsets, use total price for two 30/45W.
For bi-directional Qtz with 1 cordset, use one 100W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 14.5 | 48 |  | The CCR is typically set at step B1 (B10) or B2 (B30). Average VA load is 50% of the maximum load. For uni-directional L-850A LED, this is 15/2 = 7.5VA. For bi-directional L-850A LED, this is 29/2 = 14.5VA.
For uni-directional L-850A Qtz this is 48/2 = 24VA. For bi-directional L-850A Qtz this is (48+48)/2 = 48VA.
not used
Average Isolation Transformer load (VA) | 3 | 7.5 |  | This figure is for isolation transformer heating losses. For a 20/25W isolation transformer with an uni-directional LED L-850A, the maximum load is 6VA (3VA average). For one 30/45W transformer with a single cordset
bi-directional LED L-850A, the maximum load is 6VA (3VA average). For a 30/45W isolation transformer with a uni-directional Qtz L-850A, the maximum load is 9VA (4.5VA
average). For two 30/45W transformers with a 2 cordset bi-directional Qtz L-850A, the maximum load is 18VA total (9VA average). For one 100W transformer with a single cordset bi-directional Qtz L-850A, the maximum load is 15VA total (7.5VA average).
not used
Total Energy Savings (or Costs) per year | 1379.7 | 4375.62 | 2995.92 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 10500 | 10500 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 13495.92 |  | 11497.5 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 36463.5 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 24966 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -13495.92 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 18 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 22.2% | 2995.92 | 3.4 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 2.2 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 77.8% | 10500 | 1.5 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 13495.92
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 20695.5 | 65634.3 | -44938.8 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 157500 | -157500 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 20695.5 | 223134.3 | -202438.8
After 15 years, the total estimated reduction of emissions is 270 metric tons of CO2, or about one year's worth of emissions from 51 vehicles or 22.5 to 33 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-850A LED w Heater
| ADB SAFEGATE L-850A LED with Heater High Intensity Runway Centerline Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 150
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 74 |  |  | Consists of both fixture load (with the heater ON) and transformer losses. Enter 74VA for a bi-directional fixture with a heater and a 65W isolation transformer. Enter 36VA for uni-directional fixture with a heater and a 30/45W transformer.
Minimum ADB LED Fixture CCR Load (VA) | 42 |  |  | Consists of both fixture load (with the heater OFF) and transformer losses. Enter 42VA for a bi-directional fixture with a heater and a 65W isolation transformer. Enter 24VA for uni-directional fixture with a heater and a 30/45W transformer.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For uni-directional LED, use 30/45W. For bi-directional LED with one cordset, use 65W.
For uni-directional Qtz, use 30/45W. For bi-directional Qtz with 1 cordset, use one 100W. For bi-directional Qtz with 2 cordsets, use total price for two 30/45W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 23.19 | 57 |  | The CCR is typically set at step 1 (B10). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50% of the
Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions. The Quartz is as follows:
For a uni-directional L-850A fixture Average CCR load is (48 + 9)/2=28.5VA. For a bi-directional L-850A using one cordset, the Average CCR Load is (48 + 48 + 15)/2=55.5VA.
For a bi-directional L-850A using two cordsets and two 30/45W transformers, the Average CCR Load is (48 + 48 + 9 + 9)/2=57VA
not used
not used
Total Energy Savings (or Costs) per year | 1828.3 | 4493.88 | 2665.58 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 10500 | 10500 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 13165.58 |  | 15235.8 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 37449 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 22213.2 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -13165.58 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 16 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 20.2% | 2665.58 | 3.1 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.9 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 79.8% | 10500 | 1.4 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 13165.58
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 27424.5 | 67408.2 | -39983.7 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 157500 | -157500 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 27424.5 | 224908.2 | -197483.7
After 15 years, the total estimated reduction of emissions is 240 metric tons of CO2, or about one year's worth of emissions from 46.5 vehicles or 21 to 28.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
More information

## L-850B LED wo Heater
| ADB SAFEGATE L-850B LED without Heater High Intensity Runway Touchdown Zone Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 180
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED L-850B LED, use 20/25W. For Qtz L-850B, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 7.5 | 24 |  | The CCR is typically set at step B1 (B10) or B2 (B30). Average VA load is 50% of the maximum load. For L-850B LED, this is 15/2 = 7.5VA.
For incandescent L-850B this is 48/2 = 24VA.
not used
Average Isolation Transformer load (VA) | 1.5 | 4.5 |  | This figure is for isolation transformer heating losses. For a 20/25W isolation transformer used on LED L-850B, the maximum load is 3VA (1.5VA average). For a 30/45W isolation transformer used on Quartz L-850B, the
maximum load is 9VA (4.5VA average).
not used
Total Energy Savings (or Costs) per year | 851.47 | 2696.33 | 1844.86 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 12600 | 12600 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 14444.86 |  | 7095.6 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 22469.4 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 15373.8 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -14444.86 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 11 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 12.8% | 1844.86 | 2.1 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.3 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 87.2% | 12600 | 0.94 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 14444.86
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 12772.05 | 40444.95 | -27672.9 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 189000 | -189000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 12772.05 | 229444.95 | -216672.9
After 15 years, the total estimated reduction of emissions is 165 metric tons of CO2, or about one year's worth of emissions from 31.5 vehicles or 14.1 to 19.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-850B LED w Heater
| ADB SAFEGATE L-850B LED with Heater High Intensity Runway Touchdown Zone Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 180
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 36 |  |  | Consists of both fixture load (with the heater ON) and transformer losses. Enter 36VA for fixture with a heater and a 30/45W isolation transformer.
Minimum ADB LED Fixture CCR Load (VA) | 21 |  |  | Consists of both fixture load (with the heater OFF) and transformer losses. Enter 21VA for fixture with a heater and a 30/45W isolation transformer.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED L-850B LED with heater, use 30/45W. For Qtz L-850B, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 11.53 | 28.5 |  | The CCR is typically set at step 1 (B10). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50% of the
Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions.
The Quartz is as follows: For a L-850B fixture using a 30/45W transformer, Average CCR load is (48 + 9)/2 = 28.5VA.
not used
not used
Total Energy Savings (or Costs) per year | 1090.83 | 2696.33 | 1605.5 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 12600 | 12600 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 14205.5 |  | 9090.3 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 22469.4 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 13379.1 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -14205.5 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 9.6 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 11.3% | 1605.5 | 1.8 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.2 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 88.7% | 12600 | 0.82 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 14205.5
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 16362.45 | 40444.95 | -24082.5 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 189000 | -189000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 16362.45 | 229444.95 | -213082.5
After 15 years, the total estimated reduction of emissions is 144 metric tons of CO2, or about one year's worth of emissions from 27 vehicles or 12.3 to 18 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
More information

## L-850C,D LED wo Heater
| ADB SAFEGATE L-850C/D LED without Heater High Intensity Runway Edge and Threshold Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 150
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For uni-directional LED, use 30/45W. For bi-directional LED (with one cordset), use 65W. For bi-directional LED with 2 cordsets, use total price for two 30/45W.
For bi-directional L-850C Qtz with 1 cordset, use one 200W. L-850D Qtz with 1 cordset is 300W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 18 | 200 |  | The CCR is typically set at step B1 (B10) or B2 (B30). Average VA load is 50% of the maximum load. For uni-directional L-850D LED, this is 21/2 = 10.5VA. For bi-directional L-850C LED, this is 36/2 = 18VA.
For uni-directional L-850D Qtz this is 105/2 = 52.5VA. For bi-directional L-850C Qtz this is (105+105)/2 = 105VA.
not used
Average Isolation Transformer load (VA) | 4 | 10 |  | This figure is for isolation transformer heating losses. For a 30/45W isolation transformer with a uni-directional fixture the maximum load is 8VA (4VA average). For one 65W transformer with a single cordset bi-directional fixture the maximum load is 17VA (8.5VA average). For two 30/45W transformers with a 2 cordset bi-directional fixture the the maximum load is 16VA total (8VA average). For quartz fixtures a 100W transformer is 10VA loss (5VA average), a 200W transformer is 20VA loss (10VA average).
not used
Total Energy Savings (or Costs) per year | 1734.48 | 16556.4 | 14821.92 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 10500 | 10500 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 25321.92 |  | 14454 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 137970 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 123516 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -25321.92 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 89 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 58.5% | 14821.92 | 17 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 11 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 41.5% | 10500 | 7.6 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 25321.92
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 26017.2 | 248346 | -222328.8 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 157500 | -157500 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 26017.2 | 405846 | -379828.8
After 15 years, the total estimated reduction of emissions is 1335 metric tons of CO2, or about one year's worth of emissions from 255 vehicles or 114 to 165 homes.
© 2011-2015 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-850C,D LED w Heater
| ADB SAFEGATE L-850C/D LED with Heater High Intensity Runway Edge and Threshold Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 150
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For bi-directional LED (with one cordset), use 65W. For bi-directional with 2 cordsets, use total price for two 65W.
For bi-directional L-850C Qtz with 1 cordset, use one 200W. L-850D Qtz with 1 cordset is 300W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 32 | 200 |  | The CCR is typically set at step B1 (B10) or B2 (B30). Average VA load is 50% of the maximum load. For uni-directional L-850D LED, this is 49/2 = 24.5VA. For bi-directional L-850C LED, this is 64/2 = 32VA.
For uni-directional L-850D Qtz this is 105/2 = 52.5VA. For bi-directional L-850C Qtz this is (105+105)/2 = 105VA.
not used
Average Isolation Transformer load (VA) | 8.5 | 10 |  | This figure is for isolation transformer heating losses. For a 65W isolation transformer with a uni-directional or bi-directional fixture the maximum load is 17VA (8.5VA average). For two 65W transformers with a 2 cordset bi-directional fixture the the maximum load is 34VA total (17VA average). For quartz fixtures a 100W transformer is 10VA loss (5VA average), a 200W transformer is 20VA loss (10VA average).
not used
Total Energy Savings (or Costs) per year | 3193.02 | 16556.4 | 13363.38 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 10500 | 10500 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 23863.38 |  | 26608.5 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 137970 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 111361.5 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -23863.38 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 80 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 56% | 13363.38 | 15 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 9.7 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 44% | 10500 | 6.8 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 23863.38
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 47895.3 | 248346 | -200450.7 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 157500 | -157500 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 47895.3 | 405846 | -357950.7
After 15 years, the total estimated reduction of emissions is 1200 metric tons of CO2, or about one year's worth of emissions from 225 vehicles or 102 to 145.5 homes.
© 2011-2015 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-852A,B,C,D,J,K LED wo Heater
| ADB SAFEGATE L-852A, B, C, D and L-852J, K LED without Heater Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 200
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED, consult manufacturers catalog sheet as isolation transformer wattages vary. For uni-directional Qtz or bi-directional LED (with one cordset), use 30/45W.
For uni-directional Qtz, use 30/45W. For bi-directional Qtz with 2 cordsets, use total price for two 30/45W. For bi-directional Qtz with 1 cordset, use one 65W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 13.5 | 30 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For LED, consult manufacturers catalog sheet as loads vary. For example, a bi-directional L-852D fixture using one cordset is 27VA/2=13.5VA.
The Incandescent load is entered as follows: For a bi-directional 2 x 30W fixture, this is 60/2=30VA. For a uni-directional 1 x 30W fixture, this is 30/2=15VA; For a bi-directional 1 x 45W fixture (L-852A or L-852C), this is 45/2=22.5VA.
not used
Average Isolation Transformer load (VA) | 3 | 4.5 |  | This figure is for heating losses for the isolation transformer. For LED, consult manufacturers catalog sheet as loads vary. For example, a bi-directional L-852D fixture using one cordset and a 30/45W isolation transformer, this is 6/2 = 3VA.
|  |  | 243 | The Incandescent load is entered as follows: For a bi-directional 2 x 30W fixture, using one 65W isolation transformer, this is 13/2=6.5VA. For a bi-directional 2 x 30W fixture, using two 30/45W isolation transformers, this is (6+6)/2=6VA.
For a uni-directional 1 x 30W fixture, this is 6/2=3VA. For a bi-directional 1 x 45W fixture (L-852A or L-852C), this is 9/2=4.5VA.
not used
Total Energy Savings (or Costs) per year | 1734.48 | 3626.64 | 1892.16 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 14000 | 14000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 15892.16 |  | 14454 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 30222 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 15768 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -15892.16 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 11 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 11.9% | 1892.16 | 2.1 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.3 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 88.1% | 14000 | 0.94 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 15892.16
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 26017.2 | 54399.6 | -28382.4 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 210000 | -210000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 26017.2 | 264399.6 | -238382.4
After 15 years, the total estimated reduction of emissions is 165 metric tons of CO2, or about one year's worth of emissions from 31.5 vehicles or 14.1 to 19.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-852A,B,C,D,J,K LED w Heater
| ADB SAFEGATE L-852A, B, C, D and L-852J, K LED with Heater Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 200
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 120
Maximum ADB LED Fixture CCR Load (VA) | 71 |  |  | Consists of both fixture load (with the heater ON) and transformer losses. Consult manufacturers catalog sheet as loads vary. For example, a bi-directional L-852D fixture using one cordset is 58 (Fixture VA) + 13 (for a 65W transformer)=71VA.
Minimum ADB LED Fixture CCR Load (VA) | 40 |  |  | Consists of both fixture load (with the heater OFF) and isolation transformer losses. Consult manufacturers catalog sheet as loads vary.
For example, a bi-directional L-852D fixture using one cordset is estimated to be 27 (Fixture VA) + 13 (for a 65W transformer)=40VA.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED, consult manufacturers catalog sheet as isolation transformer wattages vary. For uni-directional Qtz or bi-directional LED (with one cordset), use 30/45W.
For uni-directional Qtz, use 30/45W. For bi-directional Qtz with 2 cordsets, use total price for two 30/45W. For bi-directional Qtz with 1 cordset, use one 65W.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 22.55 | 30 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50% of
the Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions.
The Incandescent load is entered as follows: For a bi-directional 2 x 30W fixture, this is 60/2=30VA. For a uni-directional 1 x 30W fixture, this is 30/2=15VA; For a bi-directional 1 x 45W fixture (L-852A or L-852C), this is 45/2=22.5VA.
not used
not used
Total Energy Savings (or Costs) per year | 2370.46 | 3153.6 | 783.14 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average of Incandescent lamp cost. If both lamps are replaced at the same time, use 2 x Incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 14000 | 14000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 14783.14 |  | 19753.8 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 26280 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 6526.2 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -14783.14 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 4.7 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 5.3% | 783.14 | 0.9 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.57 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 94.7% | 14000 | 0.4 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 14783.14
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 35556.9 | 47304 | -11747.1 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 210000 | -210000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 35556.9 | 257304 | -221747.1
After 15 years, the total estimated reduction of emissions is 70.5 metric tons of CO2, or about one year's worth of emissions from 13.5 vehicles or 6 to 8.6 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
More information

## L-852G LED wo Heater
| ADB SAFEGATE L-852G LED without Heater Runway Guard Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 8760 |  |  | Based on operation for 24 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture. Enter Incandescent purchase cost if you are considering LED in a new installation. Incandescent purchase cost is zero if only LED is being considered in a new
installation/replacement of an existing Incandescent installation. Note: LED Purchase price should include Y-harness adapter 70A0761 if retrofitted on a circuit using existing Power Line Carrier Remote device.
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. If new isolation transformers are being purchased: For LED, enter purchase cost of
appropriately sized isolation transformer. For Incandescent enter purchase cost of 100W transformer. If existing isolation transformers are being reused, enter zero in both cells.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 15.5 | 52.5 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For a visually monitored (Autonomous) L-852G LED using a ferroresonant CCR, this is 31/2 = 15.5VA.
For an electronically monitored L-852G LED, this is 64.1/2 = 32.05VA for both the fixture and Remote load. Note: If a Thyristor (SCR) CCR is used, contact the ADB sales dept. as loads may be higher.
The Incandescent load is entered as follows: For a visually monitored (Autonomous) L-852G, this is 105/2 = 52.5VA. For an electronically monitored L-852G, this is 130/2 = 65VA for both the fixture and Remote load.
not used
Average Isolation Transformer load (VA) | 8.2 | 7.5 |  | This figure is for isolation transformer heating losses. For a visually monitored (Autonomous) L-852G LED using a ferroresonant CCR, this is 16.4/2 = 8.2VA for a 65W transformer.
For an electronically monitored L-852G LED, this is 17.9/2 = 8.95VA for a 150W transformer. Note: If a Thyristor (SCR) CCR is used, contact the ADB sales dept. as loads may be higher.
The Incandescent load is entered as follows: For a visually monitored L-852G using a 100W isolation transformer, this is 15/2 = 7.5VA. For an electronically monitored L-852G using a 100W isolation transformer, this is 18/2 = 9VA.
not used
Total Energy Savings (or Costs) per year | 2491.34 | 6307.2 | 3815.86 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace incandescent lamps.
Average lamp replacements per year | 0 | 6 |  | Incandescent Industry Average by Customer Survey = 6
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 21000 | 21000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 24815.86 |  | 20761.2 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 52560 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 31798.8 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -24815.86 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 23 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 15.4% | 3815.86 | 4.4 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 2.8 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 84.6% | 21000 | 2 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 24815.86
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 37370.1 | 94608 | -57237.9 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 315000 | -315000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 37370.1 | 409608 | -372237.9
After 15 years, the total estimated reduction of emissions is 345 metric tons of CO2, or about one year's worth of emissions from 66 vehicles or 30 to 42 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-852G LED w Heater
| ADB SAFEGATE L-852G LED with Heater Runway Guard Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 8760 |  |  | Based on operation for 24 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 81.8 |  |  | Consists of both fixture load (with the heater ON) and transformer losses. For electronically monitored applications, also includes Remote load. For a visually monitored (Autonomous) L-852G LED using a ferroresonant CCR, this is
81.8VA using a 100W transformer. For an electronically monitored L-852G LED, this is 113.5VA using a 150W transformer. Note: If a Thyristor (SCR) CCR is used, contact the ADB sales dept. as loads may be higher.
Minimum ADB LED Fixture CCR Load (VA) | 47.4 |  |  | Consists of both fixture load (with the heater OFF) and transformer losses. For electronically monitored applications, also includes Remote load. For a visually monitored (Autonomous) L-852G LED using a ferroresonant CCR, this is
47.4VA using a 100W transformer. For an electronically monitored L-852G LED, this is 82VA using a 150W transformer. Note: If a Thyristor (SCR) CCR is used, contact the ADB sales dept. as loads may be higher.
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture. Enter Incandescent purchase cost if you are considering LED in a new installation. Incandescent purchase cost is zero if only LED is being considered in a new
installation/replacement of an existing Incandescent installation. Note: LED Purchase price should include Y-harness adapter 70A0761 if retrofitted on a circuit using existing Power Line Carrier Remote device.
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. If new isolation transformers are being purchased: For LED, enter purchase cost of
appropriately sized isolation transformer. For Incandescent enter purchase cost of 100W transformer.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 26.06 | 60 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. For electronically monitored applications,
also includes Remote load. The Average CCR LED load is computed as 50% of the Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions.
The Incandescent load is entered as follows: For a visually monitored L-852G, this is (105+15)/2 = 60VA. For an electronically monitored L-852G, this is (105+25+18)/2 = 74VA.
not used
not used
Total Energy Savings (or Costs) per year | 2739.43 | 6307.2 | 3567.77 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace incandescent lamps.
Average lamp replacements per year | 0 | 6 |  | Incandescent Industry Average by Customer Survey = 6
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 21000 | 21000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 24567.77 |  | 22828.6 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 52560 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 29731.4 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -24567.77 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 21 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 14.5% | 3567.77 | 4 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 2.5 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 85.5% | 21000 | 1.8 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 24567.77
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 41091.45 | 94608 | -53516.55 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 315000 | -315000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 41091.45 | 409608 | -368516.55
After 15 years, the total estimated reduction of emissions is 315 metric tons of CO2, or about one year's worth of emissions from 60 vehicles or 27 to 37.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
More information

## L-852T LED wo Heater
| ADB SAFEGATE L-852T LED without Heater Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED L-852T LED, use 20/25W. For Qtz L-852T, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 4000 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average Fixture Load (VA) | 9.75 | 22.5 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For L-852T LED, this is 19.5/2 = 9.75VA. For a The Quartz L-852T, this is 45/2=22.5A.
not used
Average Isolation Transformer load (VA) | 2.5 | 4.5 |  | This figure is for heating losses in the isolation transformer. For a L-852T LED, this is 5/2 = 2.5VA. For a Quartz L-852T, this is 9/2=4.5A.
not used
Total Energy Savings (or Costs) per year | 959.22 | 2010.42 | 1051.2 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Quartz Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Quartz lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 8051.2 |  | 5366.1 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 6461 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -8051.2 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 4.6 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 13.1% | 1051.2 | 0.88 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.56 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 86.9% | 7000 | 0.39 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 8051.2
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 14388.3 | 30156.3 | -15768 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 14388.3 | 135156.3 | -120768
After 15 years, the total estimated reduction of emissions is 69 metric tons of CO2, or about one year's worth of emissions from 13.2 vehicles or 5.9 to 8.4 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B23: LED Load Estimate Example 100 x 19.5 = 1950 100 x 5 = 500 1 x 300 (Wire) = 300 total = 2750 Enter 4000 for 4KW CCR
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
More information

## L-852T LED w Heater
| ADB SAFEGATE L-852T LED with Heater Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 44 |  |  | Consists of both fixture load (with the heater ON) and transformer losses. Enter 44VA for fixture with a heater and a 30/45W isolation transformer.
Minimum ADB LED Fixture CCR Load (VA) | 19.5 |  |  | Consists of both fixture load (with the heater OFF) and transformer losses. Enter 19.5VA for fixture with a heater and a 30/45W isolation transformer.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For LED L-852T LED with heater, use 30/45W. For Qtz L-852T, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 7500 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 11.43 | 27 |  | The CCR is typically set at step 1 (B10). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50% of the
Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions.
The Quartz is as follows: For a 45W fixture Average CCR load is (45 + 9)/2=27VA. The Quartz calculation assumes use of a 30/45W isolation transformer.
not used
not used
Total Energy Savings (or Costs) per year | 1192.06 | 2010.42 | 818.36 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average incandescent lamp cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 7818.36 |  | 5007.5 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 6819.6 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -7818.36 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 4.9 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 10.5% | 818.36 | 0.94 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.59 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 89.5% | 7000 | 0.42 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 7818.36
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 17880.9 | 30156.3 | -12275.4 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 17880.9 | 135156.3 | -117275.4
After 15 years, the total estimated reduction of emissions is 73.5 metric tons of CO2, or about one year's worth of emissions from 14.1 vehicles or 6.3 to 8.9 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B23: LED Load Estimate Example 100 x 44 = 4400 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5600 Enter 7500 for 7.5KW CCR
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
More information

## L-804 LED Current
| ADB SAFEGATE L-804 LED Current Driven Elevated Runway Guard Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ Near-Final Review /!\ Updated 20110303 JB Review: comments, calculations, realistic results, highlighting, margins, print area, print preview
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Total number of L-804 Wig-Wag fixtures | 20
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 8760 |  |  | Based on operation for 24 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR. Series Circuit Applications only. | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for the fixtures.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For uni-directional LED or Qtz, use 30/45W. For bi-directional LED or Qtz with 2 cordsets, use total price for two 30/45W. For bi-directional LED or Qtz with 1 cordset, use one 100W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total fixtures and Power Connection Devices.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 80% | 80% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR estimate is 85%. For a 5-step CCR estimate is 80%.
Average Fixture Load (VA) | 46 | 57.5 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For LED, consult manufacturers catalog sheet as loads vary. For example, an Instant On/Off LED L-804 is 92VA/2=46VA.
For incandescent using two 100W lamps (only one lamp On at a time), this is 115/2=57.5VA.
not used
Average Isolation Transformer load (VA) | 9 | 7.5 |  | This figure is for heating losses for the isolation transformer. For LED, consult manufacturers catalog sheet as loads vary. For example, For example, an Instant On/Off LED L-804 using a 100W transformer is 18/2=9VA.
For incandescent using two 100W lamps and a 100W transformer, this is 15/2=7.5VA.
not used
Total Energy Savings (or Costs) per year | 1156.32 | 1366.56 | 210.24 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Incandescent Lamp Cost. If both lamps are replaced at the same time, enter total Incandescent lamp costs. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 4 |  | Incandescent Industry Average by Customer Survey = 4.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 2800 | 2800 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 3010.24 |  | 9636 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11388 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 1752 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as ability to use smaller AWG supply wiring/circuit breaker & increased safety due to reduction in light outages. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -3010.24 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 1.3 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 7% | 210.24 | 0.25 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.16 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 93% | 2800 | 0.11 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 3010.24
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixture and isolation transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 17344.8 | 20498.4 | -3153.6 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 42000 | -42000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 17344.8 | 62498.4 | -45153.6
After 15 years, the total estimated reduction of emissions is 19.5 metric tons of CO2, or about one year's worth of emissions from 3.8 vehicles or 1.7 to 2.4 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-861T ETES LED wo Heater
| ADB SAFEGATE ETES L-861T LED without Heater Elevated Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For the L-861T ETES w/o heater, use 10/15W. For the L-861T Quartz-Incandescent, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 4000 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR (the type normally used on Medium Intensity runway edge circuits), estimate is 85%.
Average Fixture Load (VA) | 6 | 22.5 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For ETES LED, this is 12/2 = 6VA. For 30W lamp this is 30/2 = 15VA; For 45W lamp this is 45/2 = 22.5VA.
not used
Average Isolation Transformer load (VA) | 1.5 | 4.5 |  | This figure is for heating losses for the isolation transformer. For a 10/15W isolation transformer with an L-861T LED, the maximum load is 3VA (1.5VA average). For a 30/45W isolation transformer with an L-861T LED, the maximum load is
8.4 (4.2VA average). For a 30W Quartz-Incandescent (Q-I) lamp, transformer losses are 6VA maximum (3VA average). For 45W Q-I lamp, transformer losses are 9 VA maximum (4.5VA average).
not used
Total Energy Savings (or Costs) per year | 709.56 | 2010.42 | 1300.86 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Average of Incandescent and Quartz-Incandescent Lamp Costs is $7.75 | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Quartz-Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz-Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 8300.86 |  | 3285.6 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 8541.5 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -8300.86 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 6.1 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 15.7% | 1300.86 | 1.2 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.74 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 84.3% | 7000 | 0.52 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 8300.86
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 10643.4 | 30156.3 | -19512.9 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 10643.4 | 135156.3 | -124512.9
After 15 years, the total estimated reduction of emissions is 91.5 metric tons of CO2, or about one year's worth of emissions from 18 vehicles or 7.8 to 11.1 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B23: LED Load Estimate Example 100 x 15 = 1500 100 x 3 = 300 1 x 300 (Wire) = 300 total = 2100 Enter 4000 for 4KW CCR
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
More information

## L-861T ETES LED w Heater
| ADB SAFEGATE ETES L-861T LED with Heater Elevated Taxiway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 32.5 |  |  | Consists of both fixture load (with the heater ON) and L-830/L-831 isolation transformer losses. For LED L-861T using 20/25W Isolation Transformer, use 32.5VA. For LED L-861T using 30/45W Isolation Transformer, use 34VA.
Minimum ADB LED Fixture CCR Load (VA) | 19.5 |  |  | Consists of both fixture load (with the heater OFF) and L-830/L-831 isolation transformer losses. For LED L-861T using 20/25W Isolation Transformer, use 19.5VA. For LED L-861T using 30/45W Isolation Transformer, use 20.4VA.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For the LED L-861T ETES use 20/25W. For the L-861T Quartz-Incandescent, use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 4000 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Average CCR Load (VA) | 10.64 | 27 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50%
of the Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions. The Quartz-Incandescent (Q-I) load is entered as follows: For a 30W fixture, the
Average CCR load is (30 + 6)/2=18VA. For a 45W fixture Average CCR load is (45 + 9)/2=27VA. The Quartz-Incandescent (Q-I) calculation assumes use of a 30/45W L-830-1/L-830-2 isolation transformer.
not used
not used
Total Energy Savings (or Costs) per year | 874.6 | 2010.42 | 1135.82 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Average of Incandescent and Quartz-Incandescent Lamp Costs is $7.75 | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Quartz-Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz-Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 8135.82 |  | 4660.9 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 7166.2 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -8135.82 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 5.1 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 14% | 1135.82 | 0.98 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.62 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 86% | 7000 | 0.43 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 8135.82
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 13119 | 30156.3 | -17037.3 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 13119 | 135156.3 | -122037.3
After 15 years, the total estimated reduction of emissions is 76.5 metric tons of CO2, or about one year's worth of emissions from 14.7 vehicles or 6.5 to 9.3 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B10: Consists of 25VA fixture load + 7.5VA 20/25W transformer losses (or 9VA 30/45W transformer losses)
Note on B11: Consists of 12VA fixture load + 7.5VA 20/25W transformer losses (or 8.4VA 30/45W transformer losses)
Note on B23: LED Load Estimate Example 100 x 32.5 =3250 1 x 300 (Wire) = 300 total = 3550 Enter 4000 for 4KW CCR
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
More information

## L-861 EMIL LED wo Heater
| ADB SAFEGATE EMIL L-861 and L-861E LED without Heater Medium Intensity Runway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For L-861 EMIL w/o heater, use 20/25W. For L-861E EMIL w/o heater, use 10/15W. For L-861 Qtz-Incand., use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 4000 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR (the type normally used on Medium Intensity runway edge circuits), estimate is 85%.
Average Fixture Load (VA) | 9.8 | 22.5 |  | The CCR is typically set at step 1 (B10). Average VA load is 50% of the maximum load. For EMIL L-861 LED, this is 19.6VA/2 = 9.8VA. For bi-directional L-861E LED, this is 11.8/2 = 5.9VA.
For uni-directional L-861E LED, this is 9.9/2 = 4.95VA. For 30W lamp this is 30/2 = 15VA; For 45W lamp this is 45/2 = 22.5VA.
not used
Average Isolation Transformer load (VA) | 3.8 | 4.5 |  | This figure is for isolation transformer heating losses. For a 20/25W isolation transformer with LED L-861, the maximum load is 7.6VA (3.8VA average). For a 10/15W isolation transformer with Bi- or Uni-Directional LED L-861E, the maximum load is
6.2VA (3.1VA average). For a 30/45W isolation transformer with Qtz 30W lamp, the maximum load is 6VA (3VA average). For a 30/45W isolation transformer with Qtz 45W lamp, the maximum load is 9VA (4.5VA average).
not used
Total Energy Savings (or Costs) per year | 1030.18 | 2010.42 | 980.24 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Quartz-Incandescent Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Quartz-Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz-Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 7980.24 |  | 5957.4 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 5869.7 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -7980.24 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 4.2 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 12.3% | 980.24 | 0.8 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.51 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 87.7% | 7000 | 0.36 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 7980.24
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 15452.7 | 30156.3 | -14703.6 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 15452.7 | 135156.3 | -119703.6
After 15 years, the total estimated reduction of emissions is 63 metric tons of CO2, or about one year's worth of emissions from 12 vehicles or 5.4 to 7.7 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B23: LED Load Estimate Example 100 x 19.6 = 1960 100 x 7.6 = 760 1 x 300 (Wire) = 300 total = 3020 Enter 4000 for 4KW CCR
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for7.5KW CCR
More information

## L-861 EMIL LED w Heater
| ADB SAFEGATE EMIL L-861 and L-861E LED with Heater Medium Intensity Runway Edge Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
Number of days/year the temperature might fall below 41°F (5°C) | 100
Maximum ADB LED Fixture CCR Load (VA) | 54 |  |  | Consists of both fixture load (with the heater ON) and L-830/L-831 isolation transformer losses. For L-861, use 54VA. For Bi-Directional L-861E, use 47VA. For Uni-Directional L-861E, use 45VA.
Minimum ADB LED Fixture CCR Load (VA) | 27.2 |  |  | Consists of both fixture load (with the heater OFF) and L-830/L-831 isolation transformer losses. For L-861, use 27.2A. For Bi-Directional L-861E, use 18VA. For Uni-Directional L-861E, use 16VA.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
Capital Equipment Cost- Isolation Transformer | 0 | 0 | 0 | Investment differential for fixture isolation transformer. For L-861 EMIL and all versions of L-861E with heater, use 30/45W. For L-861 and L-861E Quartz-Incand., use 30/45W.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of fixtures and isolation transformers.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 7500 | 7500 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR (the type normally used on Medium Intensity runway edge circuits), estimate is 85%.
Average CCR Load (VA) | 15.44 | 27 |  | The CCR is typically set at step 1 (B10). Therefore, the Average CCR Load is approximately 50% of the maximum. The Average CCR Load is composed of both fixture and isolation transformer losses. The Average CCR LED load is computed as 50%
of the Maximum & Minimum CCR loads entered in the System Parameters above. Note that the heater is assumed to be on 50% of the time during colder weather conditions. The Quartz-Incandescent (Q-I) load is entered as follows: For a 30W fixture, the
Average CCR load is (30 + 6)/2=18VA. For a 45W fixture Average CCR load is (45 + 9)/2=27VA. The Quartz-Incandescent (Q-I) calculation assumes use of a 30/45W L-830-1/L-830-2 isolation transformer.
not used
not used
Total Energy Savings (or Costs) per year | 1402.83 | 2010.42 | 607.59 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Quartz-Incandescent Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Quartz-Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz-Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 7607.59 |  | 6763.8 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 11827.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 5063.3 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -7607.59 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 3.6 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 8% | 607.59 | 0.69 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.44 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 92% | 7000 | 0.31 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 7607.59
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 21042.45 | 30156.3 | -9113.85 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 21042.45 | 135156.3 | -114113.85
After 15 years, the total estimated reduction of emissions is 54 metric tons of CO2, or about one year's worth of emissions from 10.4 vehicles or 4.7 to 6.6 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
Note on B23: LED Load Estimate Example 100 x 42 = 4200 100 x 12 = 1200 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
Note on B25: Formula assumes heater is on 50% of the time when the temperature is below 41F.
Note on C23: Incandescent Load Estimate Example 100 x 45 = 4500 100 x 9 = 900 1 x 300 (Wire) = 300 total = 5700 Enter 7500 for 7.5KW CCR
More information

## L-858 Sign LED vs Non-LED
| ADB SAFEGATE L-858 LED Sign Runway and Taxiway Signs Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Other Architectures |  |  |  |  | /!\ TEST/REVIEW #1 /!\ Updated 20110304 JB TODO: Verify all text, values, calcs, fix NON-supported fixture replacement
Note: Manually enter items highlighted in yellow
System Parameters | Value |  | Other Architecture | Comment
Number of signs in Category #1 | 20 |  | 6 | Enter Sign Category #1 description here, i.e. Incandescent, Size 2,3; 3-module; Style 2 (3-step). Note: "Other Arch. Lamps per Sign" is total number of lamps within a single continuous sign.
Number of signs in Category #2 | 0 |  | 0 | Enter Sign Category #2 description here
Number of signs in Category #3 | 0 |  | 0 | Enter Sign Category #3 description here
Number of signs in Category #4 | 0 |  | 0 | Enter Sign Category #4 description here
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds: | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Other Architecture | Investment (Savings) | Comment
Capital Equipment Cost- CCR | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Sign #1 Purchase Cost. Note P/Ns below. Example: LED Mfr/Part No: ADB P/N SR33-7243110 (3-Module Style 2) Other sign Mfr/Part No: ADB P/N SH33-1241110 (Quartz 3-Module Style 2) | 0 | 0 | 0 | Investment differential for sign category #1. Enter Other Arch. purchase cost if LED is used in a new installation. Other Arch. purchase cost is zero if only LED is being used in a new/replacement of an existing Other Arch. installation.
Sign #2 Purchase Cost LED Mfr/Part No: ___«replace»___ Other sign Mfr/Part No: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign category #2.
Sign #3 Purchase Cost LED Mfr/Part No: ___«replace»___ Other sign Mfr/Part No: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign category #3.
Sign #4 Purchase Cost LED Mfr/Part No: ___«replace»___ Other sign Mfr/Part No: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign category #4.
Sign #1 Isolation Transformer Purchase Cost LED Sign XF Current Ratio/Wattage: 6.6A/6.6A; 300W Other Sign XF Current Ratio/Wattage: 6.6A/6.6A; 500W | 0 | 0 | 0 | Investment differential for sign isolation transformer #1. If more than one transformer is used, enter total Purchase Cost. Transformer purchase cost is zero if existing transformer is reused for new/replacement of an existing Other Arch. installation.
Sign #2 Isolation Transformer Purchase Cost LED Sign XF Current Ratio/Wattage: ___«replace»___ Other Sign XF Current Ratio/Wattage: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign isolation transformer #2.
Sign #3 Isolation Transformer Purchase Cost LED Sign XF Current Ratio/Wattage: ___«replace»___ Other Sign XF Current Ratio/Wattage: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign isolation transformer #3.
Sign #3 Isolation Transformer Purchase Cost LED Sign XF Current Ratio/Wattage: ___«replace»___ Other Sign XF Current Ratio/Wattage: ___«replace»___ | 0 | 0 | 0 | Investment differential for sign isolation transformer #4.
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total quantity of signs and isolation transformers.
Energy Costs and Savings | LED | Other Architecture | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step or 5.5A CCR, estimate is 85%. For a 5-step CCR, estimate is 80%.
Maximum Sign #1 CCR Load (VA) | 0 | 0 |  | Consult manufacturer's catalog sheets for load data. CCR Load includes both sign and isolation transformer load.
Maximum Sign #2 CCR Load (VA) | 0 | 0
Maximum Sign #3 CCR Load (VA) | 0 | 0
Maximum Sign #4 CCR Load (VA) | 0 | 0
Total Energy Cost per year | 0 | 0 | 0 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Other Architecture | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter replacement lamp cost. Use $14 for Quartz-Incandescent Lamp Cost. Use $12 for Fluorescent Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost, Coordinate Airfield Closure, per sign | 0 | 35 |  | Sign Industry Average by Customer Survey = $35. Assumes all lamps are replaced at the same time twice per year.
Average lamp replacements per year | 0 | 2 |  | Sign Industry Average by Customer Survey = 2.
not used
Fixture replacement rate/yr: «Not Supported» | --- | --- | --- | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 1400 | 1400 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 1400 |  | 0 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 0 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 0 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -1400 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 0 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 0% | 0 | 0 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 100% | 1400 | 0 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 1400
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Other Architecture | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixtures and transformer costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 0 | 0 | 0 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
Fixture replacement rate/yr: «Not Supported» | --- | --- | --- | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 21000 | -21000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 0 | 21000 | -21000
After 15 years, the total estimated reduction of emissions is 0 metric tons of CO2, or about one year's worth of emissions from 0 vehicles or 0 to 0 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-849-I REIL LED Current
| ADB SAFEGATE L-849-I REIL LED Current Driven Runway End Identification Lights Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Xenon |  |  |  |  | /!\ Near-Final Review /!\ Updated 20110303 JB Review: comments, calculations, realistic results, highlighting, margins, print area, print preview
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of sets of REILs | 1 |  |  | A set = 2 flash heads on the end of a runway.
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Xenon | Investment (Savings) | Comment
Capital Equipment Cost- CCR. Series Circuit Applications only. | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of fixtures used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for a set (2 flash heads) of REILs.
not used
Series Circuit Power Connection Device Purchase Cost | 0 | 0 | 0 | For L-849 Style A or Style E LED, enter price for two 200W, isolation transformers. For L-849 Style C (low intensity) LED, enter price for two 100W isolation transformers (5-step applications). For Xenon, enter price for PA-4 Power Adapter.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total sets of REILs and Power Connection Devices.
Energy Costs and Savings | LED | Xenon | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR estimate is 85%. For a 5-step CCR estimate is 80%.
Total Fixture Load (VA) | 51 | 0 |  | For a 1-step L-849 Style A (high intensity) LED REIL the fixture load is 51 + 51 = 102VA. For a 1-step L-849 Style C (low intensity) LED REIL the fixture load is 45 + 45 = 90VA. The 3-step Style E REIL is typically set at step 1 or 2. Average VA
load is 50% of the maximum load. For a L-849 Style E LED, use (51 + 51) / 2 = 51VA.
For any series-circuit-powered L-849 REIL using a xenon flash lamp, which is powered by an ADB PA4 power adaptor, enter a ZERO (0) under "Xenon". The full system load is entered in the next row as 2995VA.
not used
Series Circuit Power Connection Device load (VA) | 24 | 2995 |  | For a LED L-849 REIL using LEDs, this figure is for heating losses of the isolation transformers. For a Style A (high intensity) LED REIL using two 200W isolation transformers, this is 24 + 24 = 48VA. For a Style C (low intensity) LED REIL using
two 100W isolation transformers on a 5-step circuit, this is (15 + 15) / 2 = 15VA. The 3-step Style E REIL is typically set at step 1 or 2. Average VA load is 50% of the maximum load. For a Style E LED using two 200W isolation transformers, use
(24 + 24) / 2 = 24VA. For a L-849 Style A, C or E REIL using a xenon flash lamp and powered by a ADB PA4 power adaptor, this figure is for ALL system losses and is 2995VA.
not used
Total Energy Savings (or Costs) per year | 39.42 | 1574.17 | 1534.75 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Xenon | Savings (Cost) | Comment
Average Xenon Lamp Replacement Cost | 0 | 0 |  |  | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace one Xenon lamp.
Average replacements per year | 0 | 6 |  | Xenon Style A Industry Average by Customer Survey = 4 (2 for each unit). Xenon Style C Industry Average by Customer Survey = 2 (1 for each unit). Xenon Style E Industry Average by Customer Survey = 6 (3 for each unit).
not used
0% | 0 | 0 | 0 | Estimate of average annual REIL-set replacement rate for the lifetime of all sets of REILs (shown as % of REIL-set cost).
Routine Maintenance Cost per year | 0 | 210 | 210 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 1744.75 |  | 328.5 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 13118.1 | KWH: Total Xenon Energy Consumption per Year
Investment portion using local funds: | 0 |  | 12789.6 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Xenon is used instead of LED: | -1744.75 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 9.2 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 88% | 1534.75 | 1.8 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.1 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 12% | 210 | 0.78 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 1744.75
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Xenon | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of REIL and Power Connection Device costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Xenon REIL might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 591.3 | 23612.55 | -23021.25 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual REIL-set replacement rate for the lifetime of all sets of REILs (shown as % of REIL-set cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 3150 | -3150 | Based on routine replacements of light-sources plus labor costs over lifetime of all sets of REILs.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the REILs (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 591.3 | 26762.55 | -26171.25
After 15 years, the total estimated reduction of emissions is 138 metric tons of CO2, or about one year's worth of emissions from 27 vehicles or 11.7 to 16.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-849 REIL LED Voltage
| ADB SAFEGATE L-849 REIL LED Voltage Driven Runway End Identification Lights Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Xenon |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of sets of REILs | 1 |  |  | A set = 2 flash heads on the end of a runway.
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Xenon | Investment (Savings) | Comment
Power Supply Cost Difference | 0 | 0 | 0 | For Xenon enter total increased cost for power supply equipment. This would include the total increased cost, for example, of larger gauge wire, larger circuit breakers, fuses, supply transformer, etc. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for a set (2 flash heads) of REILs.
not used
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for power supply costs + total sets of REILs.
Energy Costs and Savings | LED | Xenon | Savings (Cost) | Comment
Energy Savings
not used
Total Fixture Load (VA) | 200 | 300 |  | For LED, consult manufacturers catalog sheet as loads vary. For example, average for a three-step L-849 Style E is (200 +200)/2 = 200VA. For a one-step LED L-849, enter only the maximum load for the two REIL units.
For Xenon, average for a three-step L-849 Style E is (300 + 300)/2 = 300VA. For a one-step Style A L-849, enter 300 + 300 = 600VA. For a one-step Style C L-849, enter 100 + 100 = 200VA.
not used
not used
Total Energy Savings (or Costs) per year | 105.12 | 157.68 | 52.56 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Xenon | Savings (Cost) | Comment
Average Xenon Lamp Replacement Cost | 0 | 0 |  |  | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace one Xenon lamp.
Average replacements per year | 0 | 6 |  | Xenon Style A Industry Average by Customer Survey = 4 (2 for each unit). Xenon Style C Industry Average by Customer Survey = 2 (1 for each unit). Xenon Style E Industry Average by Customer Survey = 6 (3 for each unit).
not used
0% | 0 | 0 | 0 | Estimate of average annual REIL-set replacement rate for the lifetime of all sets of REILs (shown as % of REIL-set cost).
Routine Maintenance Cost per year | 0 | 210 | 210 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 262.56 |  | 876 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 1314 | KWH: Total Xenon Energy Consumption per Year
Investment portion using local funds: | 0 |  | 438 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as airport operations savings due to reduced airfield down time. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Xenon is used instead of LED: | -262.56 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 0.31 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 20% | 52.56 | 0.059 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.038 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 80% | 210 | 0.026 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 262.56
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Xenon | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total costs for sets of REILs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Xenon REIL might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 1576.8 | 2365.2 | -788.4 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual REIL-set replacement rate for the lifetime of all sets of REILs (shown as % of REIL-set cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 3150 | -3150 | Based on routine replacements of light-sources plus labor costs over lifetime of all sets of REILs.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the REILs (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 1576.8 | 5515.2 | -3938.4
After 15 years, the total estimated reduction of emissions is 4.65 metric tons of CO2, or about one year's worth of emissions from 0.9 vehicles or 0.4 to 0.6 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-806, L-807 LED Current
| ADB SAFEGATE L-806 and L-807 LED Current Driven Wind Cone Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ Near-Final Review /!\ Updated 20110303 JB Review: comments, calculations, realistic results, highlighting, margins, print area, print preview
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of Wind Cones | 1
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Capital Equipment Cost- CCR. Series Circuit Applications only. | 0 | 0 | 0 | Investment differential for the circuit power supply. Do a load calculation for the quantity of Wind Cones used and determine the CCR size required. Enter the cost for each CCR. If existing CCR is being reused, enter zero in both cells. | Investment Contact the ADB Sales department for specific pricing assistance
Wind Cone Purchase Cost | 0 | 0 | 0 | Investment differential for each Wind Cone.
not used
Series Circuit Power Connection Device Purchase Cost | 0 | 0 | 0 | For LED L-806, enter price for appropriately sized isolation transformer. For incandescent L-806, enter price for PA-4 Power Adapter.
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for CCR + total Wind Cones and Power Connection Devices.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Power Supply Size Used (Watts) | 0 | 0 |  |  | Energy Savings
Average CCR Efficiency | 85% | 85% |  | Average CCR efficiency (as seen at CCRs input) of all CCR steps. For a 3-step CCR estimate is 85%. For a 5-step CCR estimate is 80%.
Total Wind Cone Fixture Load (VA) | 39.5 | 0 |  | The CCR is typically set at step 1 (B10) or 2 (B30). Average VA load is 50% of the maximum load. For LED, consult manufacturers catalog sheet as loads vary. For example, an externally lit LED L-806 without an obstruction light is 79VA/2=39.5VA.
For a series-circuit powered incandescent L-806 that is powered by an ADB PA4 power adaptor, enter a ZERO (0) under Incandescent The full CCR load is entered in the next row as 2995VA.
not used
Series Circuit Power Connection Device load (VA) | 9 | 2995 |  | This figure is for heating losses for the isolation transformer. For LED, consult manufacturers catalog sheet as loads vary. For example, an externally lit LED L-806 without an obstruction light is 18VA/2=9VA for a 150W transformer.
For an incandescent L-806 powered by a ADB PA4 power adaptor, this figure is for ALL system losses and is 2995VA.
not used
Total Energy Savings (or Costs) per year | 25.49 | 1574.17 | 1548.68 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Incandescent Lamp Cost. If all lamps are replaced at the same time, enter Incandescent lamp cost total. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per Wind Cone. | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual Wind Cone replacement rate for lifetime of all Wind Cones (shown as % of individual Wind Cone cost).
Routine Maintenance Cost per year | 0 | 70 | 70 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 1618.68 |  | 212.4 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 13118.1 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 12905.7 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as ability to use smaller AWG supply wiring/circuit breaker & increased safety due to reduction in light outages. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -1618.68 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 9.3 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 95.7% | 1548.68 | 1.8 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.1 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 4.3% | 70 | 0.79 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 1618.68
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of Wind Cone and Power Connection Device costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 382.35 | 23612.55 | -23230.2 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual Wind Cone replacement rate for lifetime of all Wind Cones (shown as % of individual Wind Cone cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 1050 | -1050 | Based on routine replacements of light-sources plus labor costs over lifetime of all Wind Cones.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the Wind Cone (such as Wind Cone refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 382.35 | 24662.55 | -24280.2
After 15 years, the total estimated reduction of emissions is 139.5 metric tons of CO2, or about one year's worth of emissions from 27 vehicles or 11.9 to 16.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-806, L-807 LED Voltage
| ADB SAFEGATE L-806 and L-807 LED Voltage Driven Wind Cone Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of Wind Cones | 1
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Power Supply Cost Difference | 0 | 0 | 0 | For Incandescent, enter total increased cost for power supply equipment. This would include the total increased cost, for example, of larger gauge wire, larger circuit breakers, fuses, supply transformer, etc. | Investment Contact the ADB Sales department for specific pricing assistance
Wind Cone Purchase Cost | 0 | 0 | 0 | Investment differential for each Wind Cone.
not used
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for power supply + total quantity of Wind Cones.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Energy Savings
not used
Wind Cone Fixture Load (VA) | 80 | 600 |  | For LED, consult manufacturers catalog sheet as loads vary. For example, an externally lit LED L-806 without an obstruction light is 80VA.. For incandescent, enter total of light source wattage.
not used
not used
Total Energy Savings (or Costs) per year | 42.05 | 315.36 | 273.31 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Incandescent Lamp Cost. If all lamps are replaced at the same time, enter Incandescent lamp cost total. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per Wind Cone. | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual Wind Cone replacement rate for lifetime of all Wind Cones (shown as % of individual Wind Cone cost).
Routine Maintenance Cost per year | 0 | 70 | 70 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 343.31 |  | 350.4 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 2628 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 2277.6 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as ability to use smaller AWG supply wiring/circuit breaker & increased safety due to reduction in light outages. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -343.31 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 1.6 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 79.6% | 273.31 | 0.31 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 0.19 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 20.4% | 70 | 0.14 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 343.31
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of Wind Cone costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 630.75 | 4730.4 | -4099.65 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual Wind Cone replacement rate for lifetime of all Wind Cones (shown as % of individual Wind Cone cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 1050 | -1050 | Based on routine replacements of light-sources plus labor costs over lifetime of all Wind Cones.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the Wind Cone (such as Wind Cone refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 630.75 | 5780.4 | -5149.65
After 15 years, the total estimated reduction of emissions is 24 metric tons of CO2, or about one year's worth of emissions from 4.7 vehicles or 2.1 to 2.9 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## L-810 LED
| ADB SAFEGATE L-810 LED Obstruction Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 25
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Power Supply Cost Difference | 0 | 0 | 0 | For Incandescent, enter total increased cost for power supply equipment. This would include the total increased cost, for example, of larger gauge wire, larger circuit breakers, fuses, supply transformer, etc. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for power supply + total quantity of fixtures.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Energy Savings
not used
Fixture Load (VA) | 9.2 | 116 |  | For a 95-277 Vac, 50/60Hz ADB L-810 single LED, enter 9.2 VA (12.2 VA with IR). For incandescent enter light source wattage. See catalog sheet for heater or other variations.
not used
not used
Total Energy Savings (or Costs) per year | 120.89 | 1524.24 | 1403.35 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Incandescent Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 105 |  | Enter the labor cost for the total time it takes to replace the incandescent L-810. Industry average cost by customer survey = $105.00 to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | For Incandescent, Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 5250 | 5250 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 6653.35 |  | 1007.4 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 12702 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 11694.6 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as ability to use smaller AWG supply wiring/circuit breaker & increased safety due to reduction in light outages. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -6653.35 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 8.4 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 21.1% | 1403.35 | 1.6 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 78.9% | 5250 | 0.71 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 6653.35
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixture costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 1813.35 | 22863.6 | -21050.25 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 78750 | -78750 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 1813.35 | 101613.6 | -99800.25
After 15 years, the total estimated reduction of emissions is 126 metric tons of CO2, or about one year's worth of emissions from 24 vehicles or 10.7 to 15 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## IUL In-pavement
| ADB SAFEGATE IUL In-pavement LED In-pavement Utility Light Life Cycle Costs, Return on Investment and Greenhouse Gas Benefits Comparison vs. Quartz-Incandescent |  |  |  |  | /!\ FINAL REVIEW /!\ Updated 20110302 JB Review: Ed's final change comments Also: comments (hide/show), print area, margins, preview, PROTECT?, final validation
Note: Manually enter items highlighted in yellow
System Parameters | Value |  |  | Comment
Number of fixtures | 100
Energy Price (present cost) per kWH | 0.12
Average Operating Time per year in hours | 4380 |  |  | Based on operation for 12 hrs/day over the course of 1 year.
Optional ROI calculation methodology. Percentage of investment using local funds | 100% |  |  | OPTIONAL method to consider the ROI calculation from the local airports perspective. If a portion of the investment uses federal or state funds, the actual local portion of the investment is much lower.
Note that the local airport still receives the full financial benefit of the entire investment compared to traditional fixtures for every year after the initial investment is paid back. Enter 100% if this investment method is not used.
not used
System Factors | LED | Incandescent | Investment (Savings) | Comment
Power Supply Cost Difference | 0 | 0 | 0 | For Incandescent, enter total increased cost for power supply equipment. This would include the total increased cost, for example, of larger gauge wire, larger circuit breakers, fuses, supply transformer, etc. | Investment Contact the ADB Sales department for specific pricing assistance
Fixture Purchase Cost | 0 | 0 | 0 | Investment differential for each fixture.
not used
not used
Total of Capital Equipment Investment |  |  | 0 | Investment differential for power supply + total quantity of fixtures.
Energy Costs and Savings | LED | Incandescent | Savings (Cost) | Comment
Energy Savings
not used
Fixture Load (VA) | 12 | 40 |  | For a 95-264 Vac, 50/60Hz ADB IUL single LED fixture, enter 12VA. For incandescent enter light source wattage.
not used
not used
Total Energy Savings (or Costs) per year | 630.72 | 2102.4 | 1471.68 | Equals differential of (Total power supply and fixture energy use x Average Operating Time per year) x (energy cost).
Maintenance Costs | LED | Incandescent | Savings (Cost) | Comment
Average Replacement Lamp Cost | 0 | 0 |  | Enter average Incandescent Lamp Cost. | Lamp and Labor Savings
Average Replace Lamp Labor; Fuel Cost; Coordinate Airfield Closure per fixture | 0 | 35 |  | Industry average cost by customer survey to replace Incandescent lamps.
Average lamp replacements per year | 0 | 2 |  | Quartz-Incandescent Industry Average by Customer Survey = 2.
not used
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost per year | 0 | 7000 | 7000 | Equals Total Replacements x (Average Lamp Cost + Average Labor and Equipment Cost).
GREEN SAVINGS
Total Yearly Savings (Energy + Lamp + Labor): | 8471.68 |  | 5256 | KWH: Total LED Energy Consumption per Year
On Total Investment of: | 0 |  | 17520 | KWH: Total Incandescent Energy Consumption per Year
Investment portion using local funds: | 0 |  | 12264 | KWH: Total Energy Consumption Reduction per Year
LED Return on Investment (ROI): | 0 | years
NOTE: ROI value should be considered as a conservative estimate because other savings may be present such as ability to use smaller AWG supply wiring/circuit breaker & increased safety due to reduction in light outages. |  |  |  | This LED product solution compared to the alternative product (as estimated above) reduces carbon emissions as estimated below. For citations and additional information click the More Information button.
Total Ongoing Energy & Labor Costs/Year if Incandescent is used instead of LED: | -8471.68 |  |  | Source: EPA Greenhouse Gas Equivalencies Calculator Reduction (Savings) of Carbon Dioxide Emissions, and Equivalent Sources
Percentage Savings due to: | % |  | 8.8 | Metric Tons: Carbon Dioxide Use of LEDs is equivalent in avoiding the Greenhouse Gas emissions of:
Energy Cost | 17.4% | 1471.68 | 1.7 | Passenger vehicles per year
Lamp Replacement Cost | 0% | 0 | 1.1 | Homes per year, due to use of electricity only
Lamp Replacement Labor | 82.6% | 7000 | 0.75 | Homes per year, due to all energy used
Capital Equip (Power + Fixture equipage) -- only if savings | n/a | 0
| 100% | 8471.68
not used
Life Cycle Cost
Fixture Lifetime (years) | 15
| LED | Incandescent | Cost (Savings) | Comment
Total System Acquisition Cost | 0 | 0 | 0 | Includes power-supply cost plus total of fixture costs.
Installation Cost | 0 | 0 | 0 | Enter installation costs for each technology. Installation costs for Incandescent might include costs for larger circuit breaker, input power wire gauge/bus bar, commercial
power transformer and larger engine generator. Enter zero in both cells if there are no differences.
Total Operating Cost (energy) | 9460.8 | 31536 | -22075.2 | Note: Energy price per kWH is assumed to remain unchanged across the full life-cycle period of the applications being compared.
0% | 0 | 0 | 0 | Estimate of average annual fixture replacement rate for the lifetime of all fixtures (shown as % of individual fixture cost).
Routine Maintenance Cost (light-source + labor only) | 0 | 105000 | -105000 | Based on routine replacements of light-sources plus labor costs over lifetime of all fixtures.
Other Maintenance Cost (over lifetime) | 0 | 0 | 0 | Enter any other maintenance costs over the lifetime of the fixtures (such as fixture refurbishment). Exclude costs covered under warranty.
Total Life Cycle Cost | 9460.8 | 136536 | -127075.2
After 15 years, the total estimated reduction of emissions is 132 metric tons of CO2, or about one year's worth of emissions from 25.5 vehicles or 11.3 to 16.5 homes.
© 2011 ADB Airfield Solutions, All Rights Reserved
This worksheet is the property of ADB Airfield Solutions and is used to estimate LCC and ROI for specific customers. It is not to be shared with any outside parties other than the customer.
More information

## ADB Green Savings Estimator
ADB Airfield Solutions “Green Savings” Estimator |  |  |  |  | Copies of Entry Cells for Tests/Restores
|  | Replaced Product Energy Consumption: | 0 | kWh / Year | Test enter val 1: | 0 | 0
|  | New LED Product Energy Consumption: | 0 | kWh / Year | Test enter val 2: | 0 | 0
|  | Reduction of Energy Consumption: | «Enter value» | kWh / Year | Test entry/calc: | «Enter value» | «Enter value»
This LED product solution, compared to the replaced product (as estimated above),
| reduces carbon emissions based on the factors cited and estimated below: |  |  |  | Calculation Analyzer / Demonstrator |  |  |  | Local-Only* Configuration for the EPA Conversion Factors, Labels, and Linked Citation URLs
| Source: | The EPA Clean Energy 'Greenhouse Gas Equivalencies Calculator' |  |  | f(x) Signif. Dgts | 2 | +1: f(x)>= | 10 | * Periodically the highlighted values in the below "Factor" cells must be verified and/or updated from the linked EPA citations.
| URL: | http://www.epa.gov/cleanenergy/energy-resources/calculator.html |  |  | Max. Round Dgts | 4 | -1: f(x)>= | 10 | Such changes must be made only within the version-controlled master copy. Contact the document owner to request updates.
| Emission | Factor (linked to EPA citation) | Estimated | Emission Reduction | f(x) ~floating~ | RD ~float~ | f(x) -SD- |  | Factor* | Units Label to be shown | EPA Citation URL
| 0.000718 | M-tons CO2/kWh (see caveats) | --- | Metric Tons CO2 | #VALUE! | #VALUE! | --- |  | 0.000718 | M-tons CO2/kWh (see caveats) | http://www.epa.gov/cleanenergy/energy-resources/refs.html
| Emission | Factor (linked to EPA citations) | Emission | Equivalencies | f(x) ~floating~ | RD ~float~ | f(x) -SD- |  | Factor* | Units Label to be shown | EPA Citation URL
| 5.23 | M-tons CO2/vehicle/year | --- | Vehicles / year | #VALUE! | #VALUE! | --- |  | 5.23 | M-tons CO2/vehicle/year | http://www.epa.gov/cleanenergy/energy-resources/refs.html#vehicles
| 0.00889 | M-tons CO2/gallon of gasoline | --- | Gallons of gasoline | #VALUE! | #VALUE! | --- |  | 0.00889 | M-tons CO2/gallon of gasoline | http://www.epa.gov/cleanenergy/energy-resources/refs.html#gasoline
| 0.43 | M-tons CO2/barrel of oil | --- | Barrels of oil | #VALUE! | #VALUE! | --- |  | 0.43 | M-tons CO2/barrel of oil | http://www.epa.gov/cleanenergy/energy-resources/refs.html#oil
| 8.24 | M-tons CO2/home/yr (electricity) | --- | Homes / year (electricity) | #VALUE! | #VALUE! | --- |  | 8.24 | M-tons CO2/home/yr (electricity) | http://www.epa.gov/cleanenergy/energy-resources/refs.html#houseelec
| 11.75 | M-tons CO2/home/yr (all energy) | --- | Homes / year (all energy) | #VALUE! | #VALUE! | --- |  | 11.75 | M-tons CO2/home/yr (all energy) | http://www.epa.gov/cleanenergy/energy-resources/refs.html#houseenergy
| 2.97 | M-tons CO2/"ton waste recycled" | --- | Tons of waste recycled | #VALUE! | #VALUE! | --- |  | 2.97 | M-tons CO2/"ton waste recycled" | http://www.epa.gov/cleanenergy/energy-resources/refs.html#recycle
| rev | 20110211 | [6 empty] | rev | 20110211
Note on E4: How to use the ADB Airfield Solutions "Green Savings" Estimator Obtain reasonable estimates for the energy (kWh) consumed per year for an LED product solution and for an alternative solution that meets the same requirements. Work with your ADB Airfield Solutions representative to obtain estimates for ADB's latest LED product solutions. Enter the estimated amounts of energy consumption for both systems into the cells for New LED and Replaced product energy consumption (which show «n/a» or blanks by default). The energy reduction will be calculated automatically, as well as the "Green Savings". Green Savings represents the estimated reduction of emissions of carbon dioxide (a greenhouse gas) based on cited emissions factors provided by the EPA. Equivalent amounts of other sources of greenhouse gases are also shown for comparison, along with their conversion factors and linked EPA citations. If you already know the amount of reduction of energy consumption (in units of kWh/Year), this value may be entered directly into the yellow cell, which shows «Enter value» by default.
Note on L4: How to use the ADB Airfield Solutions "Green Savings" Estimator Obtain reasonable estimates for the energy (kWh) consumed per year for an LED product solution and for an alternative solution that meets the same requirements. Work with your ADB Airfield Solutions representative to obtain estimates for ADB's latest LED product solutions. Enter the estimated amounts of energy consumption for both systems into the cells for New LED and Replaced product energy consumption (which show «n/a» or blanks by default). The energy reduction will be calculated automatically, as well as the "Green Savings". Green Savings represents the estimated reduction of emissions of carbon dioxide (a greenhouse gas) based on cited emissions factors provided by the EPA. Equivalent amounts of other sources of greenhouse gases are also shown for comparison, along with their conversion factors and linked EPA citations. If you already know the amount of reduction of energy consumption (in units of kWh/Year), this value may be entered directly into the yellow cell, which shows «Enter val» by default.
Note on M4: How to use the ADB Airfield Solutions "Green Savings" Estimator Obtain reasonable estimates for the energy (kWh) consumed per year for an LED product solution and for an alternative solution that meets the same requirements. Work with your ADB Airfield Solutions representative to obtain estimates for ADB's latest LED product solutions. Enter the estimated amounts of energy consumption for both systems into the cells for New LED and Replaced product energy consumption (which show «n/a» or blanks by default). The energy reduction will be calculated automatically, as well as the "Green Savings". Green Savings represents the estimated reduction of emissions of carbon dioxide (a greenhouse gas) based on cited emissions factors provided by the EPA. Equivalent amounts of other sources of greenhouse gases are also shown for comparison, along with their conversion factors and linked EPA citations. If you already know the amount of reduction of energy consumption (in units of kWh/Year), this value may be entered directly into the yellow cell, which shows «Enter val» by default.