SAMPLE SPECIFICATION

Items highlighted in yellow are to be finalized by the airport.

ITEM L-150   INSTALLATION OF ALSF-2 SEQUENCED FLASHERS

DESCRIPTION

150-1.1  This item shall consist of furnishing and installing the sequenced flashing portion of an ALSF-2 system in accordance with these specifications.

This item shall also include all wire and cable connections, the furnishing and installing of all necessary conduits and fittings and all necessary mounting structures.  It shall also include the testing of the installation and all incidentals necessary to place the flashing lights in operation as completed units to the satisfaction of the Engineer.

EQUIPMENT AND MATERIALS

150-2.1  ALSF-2.  The Approach lighting sequenced flashers shall conform to the requirements of FAA specification FAA-E-2628b, “Sequenced Flashing Lighting System, Elevated and Semiflush with Dimming and Monitoring.”  For compatibility of spare parts, Equipment supplied shall also meet FAA-E-2325, with no modification to the Individual Control Cabinets (ICCs) or Masters except for the steady burning light interface.  The ALSF-2 system shall be as manufactured by ADB SAFEGATE (www.adbsafegate.com) or approved equal.

150-2.2  EQUIPMENT SUPPLIED.  The system shall consist of 21 Elevated Sequenced Flashing Lights, 21 Individual Control Cabinets (ICC), High Voltage Interconnection Wire, 21 Junction Boxes, 1 Master Control Cabinet {with} {without} lamps-out monitoring), 1 Aiming Device, 1 Flasher Tester, 1 Spare Parts Trunk and 2 Instruction Manuals.

150-2.3  MASTER.  Input power shall be 120/240VAC, 60Hz.  The Master shall be able to accept either 120Vac or +48Vdc remote control signals.  All Control and Monitoring shall be solid state and contained on 3 PCBs located in the Master Control Cabinet.  One PCB shall be for I/O; one for the overall digital system logic and one for monitoring.  It shall be possible to delete the monitoring PCB with no effect on system control.  Control signals shall be 120Vac, generated using a zero-crossing triac to insure low RF noise is generated.  Trigger signals shall be via a positive half-wave rectified 120Vac signal using a similar triac circuit.

150-2.4  ICC.  The ICC shall develop a regulated +2000Vdc to power a PAR 56 xenon flash lamp.

The ICC shall transmit a robust monitoring feedback signal to insure signal integrity over long distances.  The monitoring feedback signal shall be via a positive half-wave rectified 120Vac signal, timed to coincide with a predefined monitoring window.

150-2.5  FLASHER TESTER.  The Flasher Tester shall check the following parameters:

- Input power to Flasher Tester.

- On/Off relay in ICC.

- Input power to ICC.

- Input power to HV DC power supply in ICC.

- Medium intensity command to ICC.

- High intensity command to ICC.

- Trigger signal to Flash Head.

It shall be possible to individually connect the Flasher Tester to a single ICC/Flash Head in order to perform troubleshooting in the maintenance shop.  The Flasher Tester shall have a trigger output to allow the lamp to be manually flashed.

150-2.6  INTERCONNECTION WIRING.  Remote control shall be by 6/C, AWG 12 wire connected only to the Master.  Power to the ICCs shall be by 3/C, AWG 10 wire daisy-chained between the Master and each ICC.  Intensity control shall be by 2/C, AWG 16 wire daisy-chained between the Master and each ICC.  {Monitoring (if used) shall be by 2/C, AWG 16 wire daisy-chained between the Master and each ICC.}  The trigger signal shall be individually connected between the Master and each ICC and shall be AWG 16 (21 total wires).

Wiring connections between the ICC and the Flash Head shall use 5 wires, each rated 12AWG, 3KV (in order to meet NEC requirements for multiple wires run in the same conduit).  The ALSF-2 manufacturer shall provide sufficient wire, in 500-foot spools, to make all interconnections between 21 Flash Heads and 21 ICCs.

CONSTRUCTION METHODS

150-3.1  PLACING THE ALSF-2 LIGHTS.  The contractor shall furnish and install a 21 light ALSF-2 sequenced flasher system as specified in the proposal and shown in the plans.  The ALSF-2 shall be mounted on poles or towers at the location shown on the plans.

150-3.2  TESTS.  The system shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance.  The test shall include the functioning of each control (Low, Medium and High) in both Remote and Local not less than 10 times at the beginning and end of the 24-hour test.  {Monitoring Tests- The lamps-out thumbwheel shall be set to 10.  No cautions or faults shall be generated at the end of the 24-hour test.}

METHOD OF MEASUREMENT

150-4.1  MEASUREMENT.  The quantity of lights to be paid for under this item shall be for 21 sequenced flashing lights, 21, Junction Boxes, High Voltage Interconnection Wire- as required, 1 Master control cabinet, 1 Spare Parts Trunk, 1 Flasher Tester and 2 Instruction Manuals installed and accepted as completed units, in place, ready for operation.

BASIS FOR PAYMENT

150-5.1  PAYMENT.  Payment will be made at the contract unit price for the completed ALSF-2 system installed, in place by the Contractor, and accepted by the Engineer.  This price shall be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools, and incidentals necessary to complete this item.

Payment will be made under:

Item L-150-5.1 	ALSF-2 system, in Place—per each

END OF ITEM L-150